**Scope of work:**

Contractor shall furnish all labor and materials in order to construct a concrete foundation and install supplied Generac SG035/ 4.5L/ 35Kw generator. Contractor shall supply all necessary materials needed to connect and power up generator. The generator shall be connected to emergency a/c units installed at site and test ran upon completion. No transfer switch is to be installed.

**Location:**

Pinecrest Supports and Service Center

Building #6924 Tots house

575 Colwell Street

Pineville, La. 71360

**Specifications:**

-Contractor shall build concrete pad, 96”x60”x6” with 1’ footings

-Contractor shall set generator supplied by Pinecrest on foundation once constructed.

-Contractor shall supply gas pipe needed to connect generator to existing shut off valve in equipment room to generator location. Approximately 120’ of 2” gas pipe will be needed.

-Contractor shall provide and install gas regulator called for by generator specs and international fuel gas code/ NFPA 54.

-Contractor shall connect generator to existing emergency a/c units on site with approximately 550’ of electrical metallic tubing (EMT) conduit and breaker panel to be supplied by contractor. Panel shall be mounted inside fenced in area to over head pipe rack structure.

-Contractor shall supply approximately 30’ by 6’ chain link fencing and extend fencing to accommodate foundation and generator with a minimum of 5’ clearance past generator pad.

-Contractor shall ensure all grounding is completed as required by code.

**Mandatory on-site visit required**:

Contact Shannon Aymond (Facility Assistant Maintenance Manager) 318-641-2288