**Warehouse Freezer with Floor**

**Brand/Model:** Amerikooler or Equal Custom build

* Interior dimension:
	+ Width: 11’-11̸8” ±4”
	+ Length: 18’-11 ½” ±4”
	+ Height: 7’-6 ¼” ±4”
* Temperature: -20 degrees
* Insulation: 4” thick AK-XPS4 or Equal extruded foam with R-values of R-32 with 50 year thermal warranty.
	+ UL classified core flame spread 15, smoke rating less than 165
	+ Hydrophic / Moisture Resistant
* Warranty: 15 year panel warranty and 1 year parts warranty **{*minimum*}**
* Finishes: interior & exterior wall/interior & exterior ceilings: 26 gauge stucco embossed acrylume
* Floor:
	+ Application: foot traffic-no rolling carts
	+ NSF floor panel rated for 700lbs. /sq. ft. , stainless steel integrated
* Door: 36” x 78” left handed flush door with brushed hardware.
	+ Heavy duty deadbolt handle latch with ¼ turn release.
	+ Regulating thermostat heater wire and heated vent.
	+ Digital LED thermometer with pilot light switch.
	+ Vapor proof 120 volt LED light fixture
	+ Interior & exterior finish: 26 gauge stucco embossed acrylume
* Accessories:
	+ Rain proof membrane with 10 ft. long termination bars/1 screw every 12 inches (membrane should be 1 ft. larger in both directions minimum)
	+ Drain hood for door 20 gauge stainless steel, with tek screws.
	+ Perimeter reinforcement floor angle (.050 thick aluminum) 1 ½” x 6” x 48” each section – supplied with stainless steel tek screws, to secure wall and floor concrete anchors (concrete anchors provided by DOC.)
	+ NSF/ DOE & ASTM compliant

**Warehouse Freezer Evaporator**

**Brand/Model** – Climate Control CEL0155BS6EEAB0403 or Equal

* Molded fan guard, NSF and UL sanitation rated
* Hinged, removable front access panels on each side providing access to electrical and refrigeration components
* Liquid line solenoid wire harness factory installed
* Sweat connections on refrigeration components
* Copper tubing with aluminum fin evaporator coils
* Electric element defrost coils and drain pan
* ¾” diameter drain hole in drain pan
* Mounted TXV { 404A}/std. solenoid
* DTFD fixed {defrost termination fan delay}
* Heater high limit switch included
* Heavy gauge aluminum cabinet {stucco}
* Power: 208-230-60-1
* BTU Capacity: 14,000 BTU 10˚ TD / -20˚ minimum

**Warehouse freezer Condensing Unit**

**Brand/Model** – Climate Control 12 x 20 CCH0055LCBCZA0300 or Equal

* Cabinet and construction
	+ Microchannel technology on condenser coils
	+ Copper tubing with aluminum fins
	+ Painted steel cabinets and corrosion protection
	+ Heavy duty steel base
	+ Air cooled
* Serviceability
	+ Service valves located outside of cabinet
	+ Receiver with fusible plug, liquid shut off valve and charging port
	+ Large electrical panel for easier access
	+ Prefabricated wiring harness connections and consistent labeling
	+ Unit stays on when hood is removed for servicing
	+ Sight glass and liquid line filter drier standard and easily visible
* Quality
	+ Leak tested, bump tested
	+ Low and high pressure controls tested
	+ Electrical circuitry tested, piping and/or vibration eliminators secured
	+ Auto-reset high pressure
	+ Adjustable low pressure control
* Additional Features
	+ Electric defrost timer
	+ Crankcase heater
	+ Low ambient control
* Power – 208-230/60/3
* BTU Capacity: Minimum 14,000 BTU @ 95˚F ambient
* R404A refrigerant compatible
* Warranty: Minimum 4 years

**-Item shall be delivered as a kit to be assembled by DOC personnel. Vendor will need to notify facility in advance of delivery and go through security at front gate. Facility has unloading means.-**