**Scope of Work:**

The Contractor shall furnish all labor and materials in order to construct a concrete foundation and install supplied generator with an automatic transfer switch for the Louisiana Department of Health (LDH).

**Location:**

R.I.S.E

4781 South Grand

Monroe, La. 71201

**Site Visit-Contact:**

Teena Wallace: (318) 362-3397

Victoria Wayne/Karen Evan: 318-362-4236

**Specifications:**

* The Contractor shall build concrete pad, 6’ x 12’ with 1’ footings
* The Contractor shall set generator supplied by ARCCO on foundation once constructed.
* The Contractor shall supply gas pipe needed to connect generator to existing shut off outside of building to generator location.
* Gas meter location is approximately 130 feet of where the generator will be installed. Therefore, pipe will need to be ran from meter to installation spot approximately 130 feet.
* The Contractor shall provide and install gas regulator called for by generator specs and international fuel gas code/ NFPA 54.
* The generator shall be connected for TX Series Automatic Transfer Switch 800 Amp, 3 pole, 120/208 VAC three phase, 60Hz, with 2-Wire Start Circuit by the Contractor.
* The panel shall be mounted inside fenced in area to overhead pipe rack structure by the Contractor.
* The Contractor shall supply chain link (gated wood) fencing and extend fencing to accommodate foundation and generator with a minimum of 5’ clearance past generator pad.
  + Fence must be constructed just outside of pad, preferably 9’ x 15’.
* The Contractor shall ensure all grounding is completed as required by code.

**Generator specifications:**

Model: SG200

Generac Industrial gaseous engine-driven generator

* Turbocharged/ aftercooler 6 cylinder 14.2L/ 200Kw generator
* Stationery Emergency- Demand Response.
* 208 KW rating wired for 120/208 VAC three phase, 60 HZ.

**General Terms/Conditions:**

* The Contractor shall supply all necessary materials needed to connect and power up the generator.
* Disposal of all materials and debris shall be the responsibility of the Contractor.
* The Contractor shall coordinate all work with agency. This includes delivery, storage, and work.