** This bid has been approved as a proprietary purchase, and only the brands and models specified will be considered. **

Scope of Work:

The Contractor shall furnish all equipment, tools, and labor to install three new generators at three locations for the Department of Corrections (DOC).

Site Visit Contact:

Will Bunch

225-634-6101

Location #1:

Gym

5568 highway 68

Jackson, LA 70748

All generator installation shall include:

- Electrical installation of new generator.

- Installation of surge protector on transfer switch.

Specifications:

- The Contractor shall remove and replace generator.

- The Contractor may have to add on to existing concrete slab.

- The Contractor shall install new wiring and necessary conduit from existing automatic transfer switch to generator.

- The Contractor shall provide 1 ½” gas stubs and install gas piping and regulator at the concrete slab.

Generator Specifications:

Brand: Kohler

Size: 150Kw

Voltage: 120/208v 60HZ 3 Phase

Alternator: 4 pole rotating field, brushless permanent magnet, 12 lead reconnect-able

Insulation NEMA MG1 Class H.

Voltage regulation no load to full load - +- .05%

Unbalanced load capability- must be 100% of rated standby current

Alternator Size: 150kw @277/480V 3Ph 60Hz

Engine: PSI 8.8L Turbocharged and Charge Cooled V-8

Rated RPM: 1800

Max Power @ rated RPM- 259HP

Fuel Type - Natural Gas

Fuel Consumption- must not exceed 1965 (CFH /FT3/HR) @ 100% load

Enclosure: Steel Sound Enclosure w/ vertical air inlet and outlet discharge

Block heater: Standard 120v 1800 watt

Battery charger: 6 amp 12vdc

A minimum of 5 years warranty on equipment

Location #2:

Highway 10 Residence

4981 Highway 10

Jackson, LA 70748

Specifications:

- The Contractor shall install new reinforced 6” concrete slab for generator.

- The Contractor shall install new automatic transfer switch on building.

- Plumbing requirement: The Contractor shall provide new low pressure regulator for house and dedicated low pressure regulator for generator once installation of transfer switch and generator are completed.

Generator Specifications:

Brand: Kohler

Size: 26kw

Voltage: 120/240 60HZ 1 Phase

Alternator: 2 pole rotating field, 4 Lead

Insulation: NEMA MG1-1.66 Class H Temp Rise 130C

Voltage regulation: No-Load to Full-Load RMS +- 1.0%

Unbalanced load capability- must be 100% of rated standby current

Alternator Size: 26kw @ 120/240v 1Ph 60Hz

Engine Specifications:

Engine: Kohler CH1006

Rated RPM: 3600

Max Power @ 36.4 HP

Fuel Type- Natural Gas or Liquid Propane

Fuel Consumption- must not exceed 290 (CFH /FT3/HR) @ 100% load

Enclosure: Aluminum Sound

Battery charger: Built-in Controller

A minimum of 5 years warranty on equipment

Automatic Transfer Switch:

Brand: Kohler

Series: RXT

Size: 200AMP

Voltage: 120/240v 60HZ 1 Phase

Quantity of switched pole: 2

Neutral Configuration: Solid

Service Rated: SERVICE RATED (with Main Breaker)

Enclosure: NEMA 3R UL Type 3R

Location #3

Compound 4 Residence

2500 Creekfield Road

Jackson, LA 70748

Specifications:

- The Contractor shall install new reinforced 6” concrete slab for generator.

- The Contractor shall install new service and new automatic transfer switch on building.

- Plumbing requirement: The Contractor shall provide a new low pressure regulator for house and dedicated low pressure regulator for generator once installation of transfer switch and generator are completed.

Generator Specifications:

Brand: Kohler

Size: 26kw

Voltage: 120/240 60HZ 1 Phase

Alternator: 2 Pole rotating field, 4 Lead

Insulation: NEMA MG1-1.66 Class H Temp Rise 130C

Voltage regulation: No-Load to Full-Load RMS +- 1.0%

Unbalanced load capability- must be 100% of rated standby current.

Alternator Size: 26kw @ 120/240v 1Ph 60Hz

Engine Specifications:

Engine: Kohler CH1006

Rated RPM: 3600

Max Power @ 36.4 HP

Fuel Type- Natural Gas or Liquid Propane

Fuel Consumption- must not exceed 290 (CFH /FT3/HR) @ 100% load

Enclosure: Aluminum Sound

Battery charger: Built-in Controller

A minimum of 5 years warranty on equipment

Automatic Transfer Switch:

Brand: Kohler

Series: RXT

Size: 200AMP

Voltage: 120/240v 60HZ 1Phase

Quantity of switched Pole: 2

Neutral Configuration: Solid

Service Rated: SERVICE RATED (with Main Breaker

Enclosure: NEMA 3R UL Type 3R

General Terms/Conditions:

- Include factory start up and demonstration to be performed with Maintenance Team on site. (May require a separate visit.)

- The Contractor shall perform power fail test and load test for 1 hour to insure proper operation of generator and transfer switch.

- Only copper wiring is approved for this project. (Includes wiring for transfer switch, generator, transformer, and control wiring)

- All work must be completed during business hours in one business day or rental generator will need to be installed to back up facility until work is completed.

- All plumbing, electrical, and starting battery for each generator shall be included by the Contractor.

- All equipment removed from site will need to delivered and off loaded at DCI Maintenance yard by the Contractor.

- All equipment shall have a minimum of 5 years warranty.