**\*\*If bidding other than specified, please provide manufacturer’s specs for “or equal” items. \*\***

**Scope of Work**

The Contractor shall supply all labor, rentals, permits and materials to replace and repair fire hydrants for the Department of Corrections (DOC).

**Location:**

DOC Allen Correctional Center

3751 Lauderdale Woodyard Rd.

Kinder, La. 70648

**Site Visit Contact:**

Taylor Maricle

337-375-6611

[Taylor.Maricle@la.gov](mailto:Taylor.Maricle@la.gov)

The Contractor shall be responsible for the following:

Fire hydrant replacement:

Brand/Model: **Mueller Super Centurion Fire Hydrant Series** or Equal

Nominal Pipe Size: 6”

Pressure Rating: A423 (250 PSI), A423HP (350 PSI)

A-2361-23 Mechanical Joint Ends

**Specify Brand/Model Bidding:** \_\_\_\_\_\_\_\_\_\_\_\_\_

* Replace fire hydrant behind maintenance shop
* Shut water off to fire hydrant
* Dig down to fire main
* Remove piping and fire hydrant from valve in the ground
* Turn water back on
* Verify no leaks are present
* Backfill and pack dirt with proper kickers in place
* Verify proper operation
* Cleaning of general work area

Fire hydrant repair:

* Investigate and repair leaking fire hydrant in front of travel trailers
* Shut water off to fire hydrant
* Dig down and investigate what is causing fire hydrant to leak from the ground
* Attempt to close drain check and fire hydrant will need to be replaced if drain check is unable to be closed.
* Install repair kit if needed.
* Verify no leaks are present and proper operation of fire hydrant
* Cleaning of general work area

**General Terms:**

* The Contractor shall schedule any water outages with facility maintenance and provide an estimation for the period of time the water will be off.
* The Contractor shall be responsible for delivery and pickup of materials/supplies needed to complete project.
* Disposal of all materials, and debris shall be the responsibility of the contractor.