**If bidding other than specified, please provide manufacturer’s specs for “or equal” items. **

Scope of Work

The Contractor shall supply all labor, rentals, permits and materials to replace and repair fire hydrants for the Department of Corrections (DOC).

Location:

DOC Allen Correctional Center

3751 Lauderdale Woodyard Rd.

Kinder, La. 70648

Site Visit Contact:

Taylor Maricle

337-375-6611

Taylor.Maricle@la.gov

The Contractor shall be responsible for the following:

Fire hydrant replacement:

Brand/Model: Mueller Super Centurion Fire Hydrant Series or Equal

Nominal Pipe Size: 6”

Pressure Rating: A423 (250 PSI), A423HP (350 PSI)

A-2361-23 Mechanical Joint Ends

Specify Brand/Model Bidding: _____________

- Replace fire hydrant behind maintenance shop

- Shut water off to fire hydrant

- Dig down to fire main

- Remove piping and fire hydrant from valve in the ground

- Turn water back on

- Verify no leaks are present

- Backfill and pack dirt with proper kickers in place

- Verify proper operation

- Cleaning of general work area

Fire hydrant repair:

- Investigate and repair leaking fire hydrant in front of travel trailers

- Shut water off to fire hydrant

- Dig down and investigate what is causing fire hydrant to leak from the ground

- Attempt to close drain check and fire hydrant will need to be replaced if drain check is unable to be closed.

- Install repair kit if needed.

- Verify no leaks are present and proper operation of fire hydrant

- Cleaning of general work area

General Terms:

- The Contractor shall schedule any water outages with facility maintenance and provide an estimation for the period of time the water will be off.

- The Contractor shall be responsible for delivery and pickup of materials/supplies needed to complete project.

- Disposal of all materials, and debris shall be the responsibility of the contractor.