## Sheet1
Line Item | Commodity/Service Description | Unit of Measure | Price
Group #1 - 20kW Towable Generator
1 | 20kW Towable Generator. 60hz, diesel fuel. Shall have an adjustable voltage to include at least 1-phase 120/240 and 3-phase 240/480. Shall include a sound attenuated enclosure. Shall be mounted on a tandem axle trailer. Shall include a trailer braking system. Shall be DOT approved for highway use. Shall include a 12/24-volt DC system. Shall include a fuel tank capable of supporting continuous operation at 100% load for at least 8 hours. Unit shall be compliant with Final Tier 4. Towable generator system shall include a minimum warranty of 1 year or 3000 hrs. Specify Brand/Model Bidding: ____________________________ | Each | ________
Group #2 - 50kW Towable Generator
2 | 50kW Towable Generator. 60hz, diesel fuel. Shall have an adjustable voltage to include at least 1-phase 120/240 and 3-phase 240/480. Shall include a sound attenuated enclosure. Shall be mounted on a tandem axle trailer. Shall include a trailer braking system. Shall be DOT approved for highway use. Shall include a 12/24-volt DC system. Shall include a fuel tank capable of supporting continuous operation at 100% load for at least 8 hours. Unit shall be compliant with Final Tier 4. Towable generator system shall include a minimum warranty of 1 year or 3000 hrs. Specify Brand/Model Bidding: ___________________________ | Each | ________
Group #3 - 100kW Towable Generator
3 | 100kW Towable Generator. 60hz, diesel fuel. Shall have an adjustable voltage to include at least 1-phase 120/240 and 3-phase 240/480. Shall include a sound attenuated enclosure. Shall be mounted on a tandem axle trailer. Shall include a trailer braking system. Shall be DOT approved for highway use. Shall include a 12/24-volt DC system. Shall include a fuel tank capable of supporting continuous operation at 100% load for at least 8 hours. Unit shall be compliant with Final Tier 4. Towable generator system shall include a minimum warranty of 1 year or 3000 hrs. Specify Brand/Model Bidding: ____________________________ | Each | ________
Group #4 - 150kW Towable Generator
4 | 150kW Towable Generator. 60hz, diesel fuel. Shall have an adjustable voltage to include at least 1-phase 120/240 and 3-phase 240/480. Shall include a sound attenuated enclosure. Shall be mounted on a tandem axle trailer. Shall include a trailer braking system. Shall be DOT approved for highway use. Shall include a 12/24-volt DC system. Shall include a fuel tank capable of supporting continuous operation at 100% load for at least 8 hours. Unit shall be compliant with Final Tier 4. Towable generator system shall include a minimum warranty of 1 year or 3000 hrs. Specify Brand/Model Bidding: ____________________________ | Each | ________
Group #5 - 200 kW Towable Generator
5 | 200 kW Towable Generator. 60hz, diesel fuel. Shall have an adjustable voltage to include at least 1-phase 120/240 and 3-phase 240/480. Shall include a sound attenuated enclosure. Shall be mounted on a tandem axle trailer. Shall include a trailer braking system. Shall be DOT approved for highway use. Shall include a 12/24-volt DC system. Shall include a fuel tank capable of supporting continuous operation at 100% load for at least 8 hours. Unit shall be compliant with Final Tier 4. Towable generator system shall include a minimum warranty of 1 year or 3000 hrs. Specify Brand/Model Bidding: ____________________________ | Each | ________
Group #6 - 250 kW Towable Generator
6 | 250 kW Towable Generator. 60hz, diesel fuel. Shall have an adjustable voltage to include at least 1-phase 120/240 and 3-phase 240/480. Shall include a sound attenuated enclosure. Shall be mounted on a tandem axle trailer. Shall include a trailer braking system. Shall be DOT approved for highway use. Shall include a 12/24-volt DC system. Shall include a fuel tank capable of supporting continuous operation at 100% load for at least 8 hours. Unit shall be compliant with Final Tier 4. Towable generator system shall include a minimum warranty of 1 year or 3000 hrs. Specify Brand/Model Bidding: ____________________________ | Each | ________
Group #7 - 300 kW Towable Generator
7 | 300 kW Towable Generator. 60hz, diesel fuel. Shall have an adjustable voltage to include at least 1-phase 120/240 and 3-phase 240/480. Shall include a sound attenuated enclosure. Shall be mounted on a tandem axle trailer. Shall include a trailer braking system. Shall be DOT approved for highway use. Shall include a 12/24-volt DC system. Shall include a fuel tank capable of supporting continuous operation at 100% load for at least 8 hours. Unit shall be compliant with Final Tier 4. Towable generator system shall include a minimum warranty of 1 year or 3000 hrs. Specify Brand/Model Bidding: ____________________________ | Each | ________
Group #8 - 400 kW Towable Generator
8 | 400 kW Towable Generator. 60hz, diesel fuel. Shall have an adjustable voltage to include at least 1-phase 120/240 and 3-phase 240/480. Shall include a sound attenuated enclosure. Shall be mounted on a tandem axle trailer. Shall include a trailer braking system. Shall be DOT approved for highway use. Shall include a 12/24-volt DC system. Shall include a fuel tank capable of supporting continuous operation at 100% load for at least 8 hours. Unit shall be compliant with Final Tier 4. Towable generator system shall include a minimum warranty of 1 year or 3000 hrs. Specify Brand/Model Bidding: ____________________________ | Each | ________
Group 9 - 500 kW Towable Generator
9 | 500 kW Towable Generator. 60hz, diesel fuel. Shall have an adjustable voltage to include at least 1-phase 120/240 and 3-phase 240/480. Shall include a sound attenuated enclosure. Shall be mounted on a tandem axle trailer. Shall include a trailer braking system. Shall be DOT approved for highway use. Shall include a 12/24-volt DC system. Shall include a fuel tank capable of supporting continuous operation at 100% load for at least 8 hours. Unit shall be compliant with Final Tier 4. Towable generator system shall include a minimum warranty of 1 year or 3000 hrs. Specify Brand/Model Bidding: ____________________________ | Each | ________
Group #10 - Generator, Stationary, 20 kW, 1-phase and Accessories
10 | Generator, Stationary, 20 kW, 1-phase, 60hz natural gas fueled connected for 1-phase, 3 wire 120/240 volts 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
11 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 10 Specify Brand/Model Bidding: _______________________ | Each | ________
12 | Enclosure: Weather Protective for generator on Line 10 Specify Brand/Model Bidding: _____________________________ | Each | ________
13 | Adder: Sound attenuation material to add to the enclosure listed on Line 12 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
Group #11 - Generator, Stationary, 20 kW, 3-phase and Accessories
14 | Generator, Stationary, 20 kW, 3-phase, 60 Hz natural gas fueled; connected for 3-phase, 4 wire 120/240 volts; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
15 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 14 Specify Brand/Model Bidding: _______________________ | Each | ________
16 | Enclosure: Weather Protective for generator on Line 14 Specify Brand/Model Bidding: _____________________________ | Each | ________
17 | Adder: Sound attenuation material to add to the enclosure listed on Line 16 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
Group #12 - Generator, Stationary, 50 kW, 3-phase and Accessories
18 | Generator, Stationary, 50 kW, 3-phase, 60 Hz natural gas fueled; connected for 3-phase, 4 wire 120/240 volts; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service Specify Brand/Model Bidding: ____________________________ | Each | ________
19 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 18 Specify Brand/Model Bidding: _______________________ | Each | ________
20 | Enclosure: Weather Protective for generator on Line 18 Specify Brand/Model Bidding: _____________________________ | Each | ________
21 | Adder: Sound attenuation material to add to the enclosure listed on Line 20 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
Group #13 - Generator, Stationary, 50 kW, 1-phase and Accessories
22 | Generator, Stationary, 50 kW, 1-phase, 60 Hz natural gas fueled; connected for 1-phase, 3 wire 120/240 volts; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
23 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 22 Specify Brand/Model Bidding: _______________________ | Each | ________
24 | Enclosure: Weather Protective for generator on Line 22 Specify Brand/Model Bidding: _____________________________ | Each | ________
25 | Adder: Sound attenuation material to add to the enclosure listed on Line 24 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
Group #14 - Generator, Stationary, 100 kW, 1-phase and Accessories
26 | Generator, Stationary, 100 kW, 1-phase, 60 Hz natural gas fueled; connected for 1-phase, 3 wire 120/240 volts; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
27 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 26 Specify Brand/Model Bidding: _______________________ | Each | ________
28 | Enclosure: Weather Protective for generator on Line 26 Specify Brand/Model Bidding: _____________________________ | Each | ________
29 | Adder: Sound attenuation material to add to the enclosure listed on Line 28 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
Group #15 - Generator, Stationary, 100 kW, 3-phase and Accessories
30 | Generator, Stationary, 100 kW, 3-phase, 60 Hz natural gas fueled; connected for 3-phase, 4 wire 120/240 volts; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service Specify Brand/Model Bidding: ____________________________ | Each | ________
31 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 30 Specify Brand/Model Bidding: _______________________ | Each | ________
32 | Enclosure: Weather Protective for generator on Line 30 Specify Brand/Model Bidding: _____________________________ | Each | ________
33 | Adder: Sound attenuation material to add to the enclosure listed on Line 32 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
Group #16 - Generator, Stationary, 150 kW, 1-phase and Accessories
34 | Generator, Stationary, 150 kW, 1-phase, 60 Hz natural gas fueled; connected for 1-phase, 3 wire 120/240 volts; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
35 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 34 Specify Brand/Model Bidding: _______________________ | Each | ________
36 | Enclosure: Weather Protective for generator on Line 34 Specify Brand/Model Bidding: _____________________________ | Each | ________
37 | Adder: Sound attenuation material to add to the enclosure listed on Line 36 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
Group #17 - Generator, Stationary, 150 kW, 3-phase and Accessories
38 | Generator, Stationary, 150 kW, 3-phase, 60 Hz natural gas fueled; connected for 3-phase, 4 wire 120/240 volts; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
39 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 38 Specify Brand/Model Bidding: _______________________ | Each | ________
40 | Enclosure: Weather Protective for generator on Line 38 Specify Brand/Model Bidding: _____________________________ | Each | ________
41 | Adder: Sound attenuation material to add to the enclosure listed on Line 40 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
Group #18 - Generator, Stationary, 200 kW, 1-phase and Accessories
42 | Generator, Stationary, 200 kW, 1-phase, 60 Hz natural gas fueled; connected for 1-phase, 3 wire 120/240 volts; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
43 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 42 Specify Brand/Model Bidding: _______________________ | Each | ________
44 | Enclosure: Weather Protective for generator on Line 42 Specify Brand/Model Bidding: _____________________________ | Each | ________
45 | Adder: Sound attenuation material to add to the enclosure listed on Line 44 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
Group #19 - Generator, Stationary, 200 kW, 3-phase and Accessories
46 | Generator, Stationary, 200 kW, 3-phase, 60 Hz natural gas fueled; connected for 3-phase, 4 wire 120/240 volts; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
47 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 46 Specify Brand/Model Bidding: _______________________ | Each | ________
48 | Enclosure: Weather Protective for generator on Line 46 Specify Brand/Model Bidding: _____________________________ | Each | ________
49 | Adder: Sound attenuation material to add to the enclosure listed on Line 48 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
Group #20 -Generator, Stationary, 300 kW, 3-phase and Accessories
50 | Generator, Stationary, 300 kW, 3-phase, 60 Hz natural gas fueled; connected for 3-phase, 4 wire 277/480 VAC; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
51 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 50 Specify Brand/Model Bidding: _______________________ | Each | ________
52 | Enclosure: Weather Protective for generator on Line 50 Specify Brand/Model Bidding: _____________________________ | Each | ________
53 | Adder: Sound attenuation material to add to the enclosure listed on Line 52 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
54 | Add a paralleling control panel to Line 50 with fully integrated microprocessor based controls allowing for complete paralleling operation without the use of traditional stand-alone type switchgear. The paralleling controller shall control the operation of each individual generator set by utilizing one digital control per generator to control all generator functions including speed governing, voltage regulation, generator set alarm and monitoring, synchronizing, load sharing, and protection. The paralleling system will allow the main power leads of each generator to be connected together at a common point of connection. The provisions for on board paralleling shall also include any other necessary unit-mounted items required such as an electrically operated circuit breaker or contactor. | Each | ________
Group #21 -Generator, Stationary, 400 kW, 3-phase and Accessories
55 | Generator, Stationary, 400 kW, 3-phase, 60 Hz natural gas fueled; connected for 3-phase, 4 wire 277/480 VAC; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
56 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 55 Specify Brand/Model Bidding: _______________________ | Each | ________
57 | Enclosure: Weather Protective for generator on Line 55 Specify Brand/Model Bidding: _____________________________ | Each | ________
58 | Adder: Sound attenuation material to add to the enclosure listed on Line 57 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
59 | Add a paralleling control panel to Line 55 with fully integrated microprocessor based controls allowing for complete paralleling operation without the use of traditional stand-alone type switchgear. The paralleling controller shall control the operation of each individual generator set by utilizing one digital control per generator to control all generator functions including speed governing, voltage regulation, generator set alarm and monitoring, synchronizing, load sharing, and protection. The paralleling system will allow the main power leads of each generator to be connected together at a common point of connection. The provisions for on board paralleling shall also include any other necessary unit-mounted items required such as an electrically operated circuit breaker or contactor. | Each | ________
Group #22 -Generator, Stationary, 500 kW, 3-phase and Accessories
60 | Generator, Stationary, 500 kW, 3-phase, 60 Hz natural gas fueled; connected for 3-phase, 4 wire 277/480 VAC; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
61 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 60 Specify Brand/Model Bidding: _______________________ | Each | ________
62 | Enclosure: Weather Protective for generator on Line 60 Specify Brand/Model Bidding: _____________________________ | Each | ________
63 | Adder: Sound attenuation material to add to the enclosure listed on Line 62 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
64 | Add a paralleling control panel to Line 60 with fully integrated microprocessor based controls allowing for complete paralleling operation without the use of traditional stand-alone type switchgear. The paralleling controller shall control the operation of each individual generator set by utilizing one digital control per generator to control all generator functions including speed governing, voltage regulation, generator set alarm and monitoring, synchronizing, load sharing, and protection. The paralleling system will allow the main power leads of each generator to be connected together at a common point of connection. The provisions for on board paralleling shall also include any other necessary unit-mounted items required such as an electrically operated circuit breaker or contactor. | Each | ________
Group #23- Generator, Stationary, 750 kW, 3-phase and Accessories
65 | Generator, Stationary, 750 kW, 3-phase, 60 Hz natural gas fueled; connected for 3-phase, 4 wire 277/480 VAC; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
66 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 65 Specify Brand/Model Bidding: _______________________ | Each | ________
67 | Enclosure: Weather Protective for generator on Line 65 Specify Brand/Model Bidding: _____________________________ | Each | ________
68 | Adder: Sound attenuation material to add to the enclosure listed on Line 67 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
69 | Add a paralleling control panel to Line 65 with fully integrated microprocessor based controls allowing for complete paralleling operation without the use of traditional stand-alone type switchgear. The paralleling controller shall control the operation of each individual generator set by utilizing one digital control per generator to control all generator functions including speed governing, voltage regulation, generator set alarm and monitoring, synchronizing, load sharing, and protection. The paralleling system will allow the main power leads of each generator to be connected together at a common point of connection. The provisions for on board paralleling shall also include any other necessary unit-mounted items required such as an electrically operated circuit breaker or contactor. | Each | ________
Group #24- Generator, Stationary, 1000 kW, 3-phase and Accessories
70 | Generator, Stationary, 1000 kW, 3-phase, 60 Hz natural gas fueled; connected for 3-phase, 4 wire 277/480 VAC; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
71 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 70 Specify Brand/Model Bidding: _______________________ | Each | ________
72 | Enclosure: Weather Protective for generator on Line 70 Specify Brand/Model Bidding: _____________________________ | Each | ________
73 | Adder: Sound attenuation material to add to the enclosure listed on Line 72 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
74 | Add a paralleling control panel to Line 70 with fully integrated microprocessor based controls allowing for complete paralleling operation without the use of traditional stand-alone type switchgear. The paralleling controller shall control the operation of each individual generator set by utilizing one digital control per generator to control all generator functions including speed governing, voltage regulation, generator set alarm and monitoring, synchronizing, load sharing, and protection. The paralleling system will allow the main power leads of each generator to be connected together at a common point of connection. The provisions for on board paralleling shall also include any other necessary unit-mounted items required such as an electrically operated circuit breaker or contactor. | Each | ________
Group #25 - Generator, Stationary, 20 kW, 1-phase and Accessories
75 | Generator, Stationary, 20 kW, 1-phase, 60hz diesel fueled; no fuel supply; connected for 1-phase, 3 wire 120/240 volts 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
76 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 75 Specify Brand/Model Bidding: _______________________ | Each | ________
77 | Enclosure: Weather Protective for generator on Line 75 Specify Brand/Model Bidding: _____________________________ | Each | ________
78 | Adder: Sound attenuation material to add to the enclosure listed on Line 77 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
79 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 75. Specify Brand/Model Bidding: ________________________ | Each | ________
Group #26 - Generator, Stationary, 20 kW, 3-phase and Accessories
80 | Generator, Stationary, 20 kW, 3-phase, 60hz diesel fueled; no fuel supply; connected for 3-phase, 4 wire 120/240 volts 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
81 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 80 Specify Brand/Model Bidding: _______________________ | Each | ________
82 | Enclosure: Weather Protective for generator on Line 80 Specify Brand/Model Bidding: _____________________________ | Each | ________
83 | Adder: Sound attenuation material to add to the enclosure listed on Line 82 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
84 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 80. Specify Brand/Model Bidding: ________________________ | Each | ________
Group #27 - Generator, Stationary, 50 kW, 1-phase and Accessories
85 | Generator, Stationary, 50 kW, 1-phase, 60hz diesel fueled; no fuel supply; connected for 1-phase, 3 wire 120/240 volts 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
86 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 85 Specify Brand/Model Bidding: _______________________ | Each | ________
87 | Enclosure: Weather Protective for generator on Line 85 Specify Brand/Model Bidding: _____________________________ | Each | ________
88 | Adder: Sound attenuation material to add to the enclosure listed on Line 87 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
89 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 85. Specify Brand/Model Bidding: ________________________ | Each | ________
Group #28 - Generator, Stationary, 50 kW, 3-phase and Accessories
90 | Generator, Stationary, 50 kW, 3-phase, 60hz diesel fueled; no fuel supply; connected for 3-phase, 4 wire 120/240 volts 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
91 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 90 Specify Brand/Model Bidding: _______________________ | Each | ________
92 | Enclosure: Weather Protective for generator on Line 90 Specify Brand/Model Bidding: _____________________________ | Each | ________
93 | Adder: Sound attenuation material to add to the enclosure listed on Line 92 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
94 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 90. Specify Brand/Model Bidding: ________________________ | Each | ________
Group #29 - Generator, Stationary, 100 kW, 1-phase and Accessories
95 | Generator, Stationary, 100 kW, 1-phase, 60hz diesel fueled; no fuel supply; connected for 1-phase, 3 wire 120/240 volts 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
96 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 95 Specify Brand/Model Bidding: _______________________ | Each | ________
97 | Enclosure: Weather Protective for generator on Line 95 Specify Brand/Model Bidding: _____________________________ | Each | ________
98 | Adder: Sound attenuation material to add to the enclosure listed on Line 97 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
99 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 95. Specify Brand/Model Bidding: ________________________ | Each | ________
Group #30 - Generator, Stationary, 100 kW, 3-phase and Accessories
100 | Generator, Stationary, 100 kW, 3-phase, 60hz diesel fueled; no fuel supply; connected for 3-phase, 4 wire 120/240 volts 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
101 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 100 Specify Brand/Model Bidding: _______________________ | Each | ________
102 | Enclosure: Weather Protective for generator on Line 100 Specify Brand/Model Bidding: _____________________________ | Each | ________
103 | Adder: Sound attenuation material to add to the enclosure listed on Line 102 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
104 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 100. Specify Brand/Model Bidding: ________________________ | Each | ________
Group #31 - Generator, Stationary, 150 kW, 1-phase and Accessories
105 | Generator, Stationary, 150 kW, 1-phase, 60hz diesel fueled; no fuel supply; connected for 1-phase, 3 wire 120/240 volts 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
106 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 105 Specify Brand/Model Bidding: _______________________ | Each | ________
107 | Enclosure: Weather Protective for generator on Line 105 Specify Brand/Model Bidding: _____________________________ | Each | ________
108 | Adder: Sound attenuation material to add to the enclosure listed on Line 107 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
109 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 105. Specify Brand/Model Bidding: ________________________ | Each | ________
Group #32 - Generator, Stationary, 150 kW, 3-phase and Accessories
110 | Generator, Stationary, 150 kW, 3-phase, 60hz diesel fueled; no fuel supply; connected for 3-phase, 4 wire 120/240 volts 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
111 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 110 Specify Brand/Model Bidding: _______________________ | Each | ________
112 | Enclosure: Weather Protective for generator on Line 110 Specify Brand/Model Bidding: _____________________________ | Each | ________
113 | Adder: Sound attenuation material to add to the enclosure listed on Line 112 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
114 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 110. Specify Brand/Model Bidding: ________________________ | Each | ________
Group #33 - Generator, Stationary, 200 kW, 1-phase and Accessories
115 | Generator, Stationary, 200 kW, 1-phase, 60hz diesel fueled; no fuel supply; connected for 1-phase, 3 wire 120/240 volts 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
116 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 115 Specify Brand/Model Bidding: _______________________ | Each | ________
117 | Enclosure: Weather Protective for generator on Line 115 Specify Brand/Model Bidding: _____________________________ | Each | ________
118 | Adder: Sound attenuation material to add to the enclosure listed on Line 117 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
119 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 115. Specify Brand/Model Bidding: ________________________ | Each | ________
Group #34 - Generator, Stationary, 200 kW, 3-phase and Accessories
120 | Generator, Stationary, 200 kW, 3-phase, 60hz diesel fueled; no fuel supply; connected for 3-phase, 4 wire 120/240 volts 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
121 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 120 Specify Brand/Model Bidding: _______________________ | Each | ________
122 | Enclosure: Weather Protective for generator on Line 120 Specify Brand/Model Bidding: _____________________________ | Each | ________
123 | Adder: Sound attenuation material to add to the enclosure listed on Line 122 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
124 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 120. Specify Brand/Model Bidding: ________________________ | Each | ________
Group #35 - Generator, Stationary, 250 kW, 1-phase and Accessories
125 | Generator, Stationary, 250 kW, 1-phase, 60hz diesel fueled; no fuel supply; connected for 1-phase, 3 wire 120/240 volts 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
126 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 125 Specify Brand/Model Bidding: _______________________ | Each | ________
127 | Enclosure: Weather Protective for generator on Line 125 Specify Brand/Model Bidding: _____________________________ | Each | ________
128 | Adder: Sound attenuation material to add to the enclosure listed on Line 127 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
129 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 125. Specify Brand/Model Bidding: ________________________ | Each | ________
Group #36 - Generator, Stationary, 250 kW, 3-phase and Accessories
130 | Generator, Stationary, 250 kW, 3-phase, 60hz diesel fueled; no fuel supply; connected for 3-phase, 4 wire 120/240 volts 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
131 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 130 Specify Brand/Model Bidding: _______________________ | Each | ________
132 | Enclosure: Weather Protective for generator on Line 130 Specify Brand/Model Bidding: _____________________________ | Each | ________
133 | Adder: Sound attenuation material to add to the enclosure listed on Line 132 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
134 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 130. Specify Brand/Model Bidding: ________________________ | Each | ________
Group #37 - Generator, Stationary, 300 kW, 3-phase and Accessories
135 | Generator, Stationary, 300 kW, 3-phase, 60hz diesel fueled; no fuel supply; connected for 3-phase, 4 wire 120/240 volts 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
136 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 135 Specify Brand/Model Bidding: _______________________ | Each | ________
137 | Enclosure: Weather Protective for generator on Line 135 Specify Brand/Model Bidding: _____________________________ | Each | ________
138 | Adder: Sound attenuation material to add to the enclosure listed on Line 137 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
139 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 135. Specify Brand/Model Bidding: ________________________ | Each | ________
Group #38 - Generator, Stationary, 350 kW, 3-phase and Accessories
140 | Generator, Stationary, 350 kW, 3-phase, 60hz diesel fueled; no fuel supply; connected for 3-phase, 4 wire 120/240 volts 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
141 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 140 Specify Brand/Model Bidding: _______________________ | Each | ________
142 | Enclosure: Weather Protective for generator on Line 140 Specify Brand/Model Bidding: _____________________________ | Each | ________
143 | Adder: Sound attenuation material to add to the enclosure listed on Line 142 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
144 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 140 Specify Brand/Model Bidding: ________________________ | Each | ________
Group #39 - Generator, Stationary, 400 kW, 3-phase and Accessories
145 | Generator, Stationary, 400 kW, 3-phase, 60hz diesel fueled; no fuel supply; connected for 3-phase, 4 wire 120/240 volts 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
146 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 145 Specify Brand/Model Bidding: _______________________ | Each | ________
147 | Enclosure: Weather Protective for generator on Line 145 Specify Brand/Model Bidding: _____________________________ | Each | ________
148 | Adder: Sound attenuation material to add to the enclosure listed on Line 147 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _______________________ | Each | ________
149 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 145. Specify Brand/Model Bidding: ________________________ | Each | ________
Group #40 - Generator, Stationary, 500 kW, 3-phase and Accessories
150 | Generator, Stationary, 500 kW, 3-phase, 60hz diesel fueled; no fuel supply; connected for 3-phase, 4 wire 277/480 VAC; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
151 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 150 Specify Brand/Model Bidding: _______________________ | Each | ________
152 | Enclosure: Weather Protective for generator on Line 150 Specify Brand/Model Bidding: _____________________________ | Each | ________
153 | Adder: Sound attenuation material to add to the enclosure listed on Line 152. Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
154 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 150. Specify Brand/Model Bidding: ________________________ | Each | ________
155 | Add a paralleling control panel to Line 150 with fully integrated microprocessor based controls allowing for complete paralleling operation without the use of traditional stand-alone type switchgear. The paralleling controller shall control the operation of each individual generator set by utilizing one digital control per generator to control all generator functions including speed governing, voltage regulation, generator set alarm and monitoring, synchronizing, load sharing, and protection. The paralleling system will allow the main power leads of each generator to be connected together at a common point of connection. The provisions for on board paralleling shall also include any other necessary unit-mounted items required such as an electrically operated circuit breaker or contactor. | Each | ________
Group #41 - Generator, Stationary, 600 kW, 3-phase and Accessories
156 | Generator, Stationary, 600 kW, 3-phase, 60hz diesel fueled; no fuel supply; connected for 3-phase, 4 wire 277/480 VAC; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
157 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 156 Specify Brand/Model Bidding: _______________________ | Each | ________
158 | Enclosure: Weather Protective for generator on Line 156 Specify Brand/Model Bidding: _____________________________ | Each | ________
159 | Adder: Sound attenuation material to add to the enclosure listed on Line 158 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
160 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 156. Specify Brand/Model Bidding: ________________________ | Each | ________
161 | Add a paralleling control panel to Line 156 with fully integrated microprocessor based controls allowing for complete paralleling operation without the use of traditional stand-alone type switchgear. The paralleling controller shall control the operation of each individual generator set by utilizing one digital control per generator to control all generator functions including speed governing, voltage regulation, generator set alarm and monitoring, synchronizing, load sharing, and protection. The paralleling system will allow the main power leads of each generator to be connected together at a common point of connection. The provisions for on board paralleling shall also include any other necessary unit-mounted items required such as an electrically operated circuit breaker or contactor. | Each | ________
Group #42 - Generator, Stationary, 750 kW, 3-phase and Accessories
162 | Generator, Stationary, 750 kW, 3-phase, 60hz diesel fueled; no fuel supply; connected for 3-phase, 4 wire 277/480 VAC; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
163 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 162 Specify Brand/Model Bidding: _______________________ | Each | ________
164 | Enclosure: Weather Protective for generator on Line 162 Specify Brand/Model Bidding: _____________________________ | Each | ________
165 | Adder: Sound attenuation material to add to the enclosure listed on Line 164 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
166 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 162. Specify Brand/Model Bidding: ________________________ | Each | ________
167 | Add a paralleling control panel to Line 162 with fully integrated microprocessor based controls allowing for complete paralleling operation without the use of traditional stand-alone type switchgear. The paralleling controller shall control the operation of each individual generator set by utilizing one digital control per generator to control all generator functions including speed governing, voltage regulation, generator set alarm and monitoring, synchronizing, load sharing, and protection. The paralleling system will allow the main power leads of each generator to be connected together at a common point of connection. The provisions for on board paralleling shall also include any other necessary unit-mounted items required such as an electrically operated circuit breaker or contactor. | Each | ________
Group #43 - Generator, Stationary, 1000 kW, 3-phase and Accessories
168 | Generator, Stationary, 1000 kW, 3-phase, 60hz diesel fueled; no fuel supply; connected for 3-phase, 4 wire 277/480 VAC; 12 lead reconnectable lead connection. Stationary generator system shall include a minimum 5 year or 1500 hour parts and labor warranty to begin when system is first placed in service. Specify Brand/Model Bidding: ____________________________ | Each | ________
169 | Remote Annunciator: 12 or 24 volt, NFPA110 compliant for generator on Line 168 Specify Brand/Model Bidding: _______________________ | Each | ________
170 | Enclosure: Weather Protective for generator on Line 168 Specify Brand/Model Bidding: _____________________________ | Each | ________
171 | Adder: Sound attenuation material to add to the enclosure listed on Line 170 Sound material to reduce sound level of WP enclosure to meet 80 dba req. Specify Brand/Model Bidding: _____________________________ | Each | ________
172 | Fuel Storage Tank: A sub-base, double wall type, diesel fuel storage tank with a minimum of 24 hours run time at full load storage capacity. For generator on Line 168. Specify Brand/Model Bidding: ________________________ | Each | ________
173 | Add a paralleling control panel to Line 168 with fully integrated microprocessor based controls allowing for complete paralleling operation without the use of traditional stand-alone type switchgear. The paralleling controller shall control the operation of each individual generator set by utilizing one digital control per generator to control all generator functions including speed governing, voltage regulation, generator set alarm and monitoring, synchronizing, load sharing, and protection. The paralleling system will allow the main power leads of each generator to be connected together at a common point of connection. The provisions for on board paralleling shall also include any other necessary unit-mounted items required such as an electrically operated circuit breaker or contactor. | Each | ________
Group #44 - Automatic Transfer Switches
174 | Automatic Transfer Switch, 100 AMPS Continuous at 1-phase, 3 wire, 120/240 volts. ATS shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding: ____________________________ | Each | ________
175 | Automatic Transfer Switch, 100 AMPS Continuous at 3-phase, 4 wire, 120/240 volts. ATS shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding: ____________________________ | Each | ________
176 | Automatic Transfer Switch, 200 AMPS Continuous at 1-phase, 3 wire, 120/240 volts. ATS shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding: ____________________________ | Each | ________
177 | Automatic Transfer Switch, 200 AMPS Continuous at 3-phase, 4 wire, 120/240 volts. ATS shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding: ____________________________ | Each | ________
178 | Automatic Transfer Switch, 300 AMPS Continuous at 1-phase, 3 wire, 120/240 volts. ATS shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding: ____________________________ | Each | ________
179 | Automatic Transfer Switch, 300 AMPS Continuous at 3-phase, 4 wire, 120/240 volts. ATS shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding: ____________________________ | Each | ________
180 | Automatic Transfer Switch, 400 AMPS Continuous at 1-phase, 3 wire, 120/240 volts. ATS shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding: ____________________________ | Each | ________
181 | Automatic Transfer Switch, 400 AMPS Continuous at 3-phase, 4 wire, 120/240 volts. ATS shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding: ____________________________ | Each | ________
182 | Automatic Transfer Switch, 600 AMPS Continuous at 1-phase, 3 wire, 120/240 volts. ATS shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding: ____________________________ | Each | ________
183 | Automatic Transfer Switch, 600 AMPS Continuous at 3-phase, 4 wire, 120/240 volts. ATS shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding: ____________________________ | Each | ________
184 | Automatic Transfer Switch, 800 AMPS Continuous at 3-phase, 4 wire, 120/240 volts. ATS shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding: ____________________________ | Each | ________
185 | Automatic Transfer Switch, 1000 AMPS Continuous at 3-phase, 4 wire, 120/240 volts. ATS shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding: ____________________________ | Each | ________
186 | Automatic Transfer Switch, 1200 AMPS Continuous at 3-phase, 4 wire, 120/240 volts. ATS shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding: ____________________________ | Each | ________
187 | Automatic Transfer Switch, 1600 AMPS Continuous at 3-phase, 4 wire, 120/240 volts. ATS shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding: ____________________________ | Each | ________
188 | Automatic Transfer Switch, 2000 AMPS Continuous at 3-phase, 4 wire, 120/240 volts. ATS shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding: ____________________________ | Each | ________
189 | Automatic Transfer Switch, 2600 AMPS Continuous at 3-phase, 4 wire, 120/240 volts. ATS shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding: ____________________________ | Each | ________
190 | Automatic Transfer Switch, 3000 AMPS Continuous at 3-phase, 4 wire, 120/140 volts. ATS Shall include a minimum 5 year parts and labor warranty. Specify Brand/Model Bidding:_____________________________ | Each | ________