State of Louisiana

Office of State Procurement

Jeff Landry

Governor

Taylor F. Barras

Commissioner of Administration

Division of Administration

1201 N. Third Street, Suite 2-160

Baton Rouge, Louisiana 70802-5243

Phone (225) 342-8010

Fax (225) 342-9756

December 15, 2025

# ADDENDUM NO. 01

Your reference is directed to RFx Number 3000025545 for the Invitation to Bid (ITB) for the State of Louisiana Generators Towable and Stationary - Statewide, which is currently scheduled to open at 10:00 AM CT on December 29, 2025.

******************************************************************************

The following are the Vendor’s Inquiries received by the deadline date of December 8, 2025 and the State’s Responses:

Vendor’s Inquiry #1: Would a certified factory load bank test, with documented results, be acceptable? (as opposed to a load bank test at every site)

a. As the generator manufacturer, we have the proper equipment onsite to perform the

required load bank tests, as described in the BID documents.

b. During the startup and commissioning of each unit, we still do a transfer test and

building load test (this is what’s important – to make sure the selected generator can

carry the desired load and performs as designed)

c. There is a substantial cost saving to the State of Louisiana by not having load bank

equipment and cables shipped and set up at every site, for testing purposes only.

- State’s Response #1: According to Attachment B Generator Specifications, page 7, Load Bank Testing: At the time of initial startup and check-out of the standby power system by the supplier, they shall furnish load banks as required, with the operator to perform the duties listed on pg.7. The specifications will remain as written.

Vendor’s Inquiry #2: For the purpose of calculating freight charges, please confirm ship to locations for each generator and ATS.

- State’s Response #2: The ship to locations are unknown at this time. As stated in Attachment A – Special Terms and Conditions, page 5, Orders All State Agencies are to issue contract purchase orders for the items required, as and when needed.

******************************************************************************

All else remains as on original bid.

******************************************************************************

THIS ADDENDUM IS HEREBY OFFICIALLY MADE A PART OF THE REFERENCED SOLICITATION.

ACKNOWLEDGEMENT: If you have already submitted your bid and this Addendum does not cause you to revise your bid, you should acknowledge receipt of this Addendum by identifying your business name and by signing where indicated. You may return this Acknowledgement by mail or delivery by hand or courier  to: Office of State Procurement, 1201 N. 3rd Street, Ste. 2-160, Baton Rouge, LA 70802, or by fax to: (225) 342- 9756. The State reserves the right to request a completed Acknowledgement at any time. Failure to execute an Acknowledgement shall not relieve the bidder from complying with the terms of its bid.

Addendum Acknowledged/No changes:

For: ________________________  	By: ________________________

REVISION: If you have already submitted your bid and this Addendum requires you to revise your bid, you must indicate any change(s) below, identify your business name and sign where shown. Revisions shall be delivered prior to bid opening by mail or delivery by hand  or courier to: Office of State Procurement, 1201 N. 3rd Street, Ste. 2-160, Baton Rouge, LA 70802, and indicate the RFx number and the bid opening date and time on the outside of the envelope for proper identification, or by fax to: (225) 342-9756. Electronic transmissions other than by fax are not being accepted at this time.

Revisions received after bid opening shall not be considered and you shall be held to your original bid.

Revision:

For: ________________________  	By: ________________________

By:	Donald Hunter

Office of State Procurement Telephone No. 225-342-5484 Email: Donald.Hunter2@la.gov