**If bidding other than specified, please provide manufacturer’s specs for “or equal” items. **

Scope of Work:

The Contractor shall furnish all labor, materials, tools, and equipment necessary to install a diesel generator and an automatic transfer switch for the Eastern LA Mental Health System (ELMHS).

Location:

Eastern Mental Health System (Parker Kitchen Facility)

4502 Hwy 951

Jackson, LA 70748

Agency Contact

Jonathan Holley or Dylan Fury

225-634-0202

Specifications:

The Contractor shall be responsible for the following:

- Diesel Generator

  - Blue Star JD-200-01 or Equal

Specify Brand/Model Bidding: ____________________

  - Rating: 120/208V, 3 Phase, 60Hz

  - KW: 200kw

  - Deep Sea Controller with Remote Annunciator Panel

  - Emergency Stop Kit

  - Level 1 Weather Enclosure, powder-coated, 14-gauge steel, 200 MPH wind-rated

  - Critical Grade Exhaust Silencer

  - 96-hour (1,500-gallon) UL-142 Double Wall Sub-base Fuel Tank

  - 700 Amp, 3-Pole, 600V Main Circuit Breaker

  - Engine Block Heater: 2000W, 240V

  - 12V 10A Battery Charger

  - 2-Year / 2,000-Hour Limited Warranty

- Generator Installation

  - Set and secure generator on the prepared concrete pad.

  - Install all required control cables, main power cables, and two dedicated circuits for the battery charger and block heater.

- Automatic Transfer Switch (ATS)

  - ASCO 300 Series or Equal

Specify Brand/Model Bidding: ____________________

- Rating: 600A, 208V, 60Hz, 3 Phase

- Controller: 300 Series with 11BE Exerciser Kit

- Non-Service Rated, 3-Pole with Solid Neutral, Open Transition

- NEMA 3R Enclosure with 44G Strip Heater

- 2-Year Limited Warranty

- ATS Installation

  - Mount and secure ATS on concrete pad.

  - Coordinate scheduled shutdown for final connection between ATS, building service, and transformer.

  - Terminate and label all power and control wiring per code and manufacturer standards.

- Concrete Foundation

  - Generator Pad: Reinforced with rebar; 20 ft x 20 ft x 3 ft.

  - ATS Pad: Reinforced with rebar; 7 ft x 4 ft x 2 ft.

  - Concrete to meet applicable structural standards for equipment loading and vibration control.

- Fencing

  - Install 6 ft chain-link security fence around generator and ATS area, including one lockable access gate.

- Remote Annunciator Panel and Remote Emergency Stop

- Install conduit from generator through concrete slab to building.

- Mount and wire remote annunciator panel inside building.

- Install remote emergency stop button in a breaker glass enclosure in an accessible and code-compliant location.

- Fueling

  - Supply and fill fuel to 80% of tank capacity using #2 Off-Road Diesel with fuel stabilizer.

- Load Testing

  - Perform 2-hour load bank test:

    - 30 minutes at 50% load

    - 1.5 hours at 80% load

  - Conduct 1-hour building load transfer test (to be coordinated with owner’s representative).

- Functional Testing

  - Verify all generator and ATS operations, alarms, safety interlocks, and control functions.

  - Confirm proper function of remote annunciator and emergency stop circuits.

- Training and Demonstration

  - Conduct operational demonstration with the project coordinator and facility maintenance personnel.

  - Provide training on start-up, shut-down, fault response, and maintenance requirements.

General Terms/Conditions:

- All work shall comply with local building, electrical, and fire codes.

- The Contractor shall coordinate with facility management to minimize downtime.

- The Contractor shall provide all necessary equipment, labor, materials, and permits.

- All materials and workmanship shall be guaranteed for a minimum of one year from final acceptance unless otherwise stated by manufacturer warranty.

- On site work schedule is Monday – Friday, 7:00am to 3:30pm