# Revised Attachment B - Specifications  (rev 2/25/26)

RFx number: 3000025881    Contract Title: HVAC Services for LDWF Headquarter Campus

Scope of Work

These specifications outline services needed for the heating, ventilation, and air conditioning (HVAC) equipment at the Louisiana Department of Wildlife and Fisheries (LDWF) headquarters campus located at 2000 Quail Drive, Baton Rouge, LA  70808.

This service contract must include:

- Semi-annual preventative maintenance inspections and testing of equipment listed on page four to maintain optimal condition and efficiency.

- On-call/After-Hours/Weekend and Holidays service hourly rate. Materials as needed.

- This is not an all-inclusive contract.

When inspecting, testing or servicing HVAC equipment, the Contractor must adhere to all manufacturers’ recommendations regarding maintenance, up keep, and repair. Appendix A, to this Attachment B, includes a list of all equipment to be serviced at the above-mentioned location. Contractor to attain a copy of the manufacturers’ recommendations for all equipment listed will be provided at the mandatory pre-bid jobsite visit. If new equipment not listed in Appendix A, to this Attachment B, is purchased for the above-mentioned location, the Contractor must be consulted prior to the purchase to assess service capabilities. The Contractor will provide all manufacturer recommendations on the newly acquired equipment to the User Agency and must assume responsibility for semi-annual inspections and on-call servicing.

Semi-Annual Preventative Maintenance Inspection and Testing (see Appendix B)

The Contractor’s responsibility is to conduct the appropriate preventative maintenance inspections and testing on all HVAC equipment and perform all work necessary to assure a complete, dependable and operational system. The Contractor must adhere to all manufacturers’ recommendations. Typical activities for the semi-annual HVAC preventative maintenance inspections and testing include but are not limited to:

- Inspecting for worn, failed or doubtful parts; mountings; drive couplings; oil level; rotation; soot; flame composition and shape; pilot and igniter; steam; water; oil and/oil refrigerant leaks, etc.

- Cleaning coil surfaces; fan impellers and blades; electrical contacts; burner orifices; passages and nozzles; pilot and igniter; cooling tower baffles, basin, sump and float; chiller, condenser, water strainers, filters and boiler tubes, etc.

- Aligning belt drives; drive couplings; air fins, etc.

- Calibrating safety controls; temperature and pressure controls, etc.

- Tightening electrical connections; mounting bolts; pipe clamps; refrigerant piping fittings; damper sections, etc.

- Adjusting belt tension; refrigerant charge; super heat; fan RPM; water chemical feed and feed rate; burner fuel/air ratios; gas pressure; set point of controls and limits; compressor cylinder unloaders; damper close-off; sump floats, etc.

- Lubricating motors; fan and damper bearings; valve stems; damper linkages; fan vane linkages, etc.

- Painting, for corrosion control, as directed by our scheduling system and on an as-needed basis.

- Testing for excessive vibration; motor winding resistance; refrigerant charge; fan RPM; refrigerant oil (acid); water conditions; flue gas analysis; safety controls; combustion and draft crankcase heaters; controls system(s), etc.

Special Note: The Contractor is to abide by all refrigerant laws in place at the time of service.  Neither the State of Louisiana nor any of its employees will assume responsibility for the Contractor’s non-compliance.

Special Note: This agreement excludes monthly filter changes.

Scheduling for semi-annual inspections and testing will be initiated by the LDWF Maintenance Superintendent or his designee. Scheduling shall take place during normal business hours (7:00 a.m. to 4:30 p.m. CT) Monday through Friday, excluding LDWF holidays, unless authorized by LDWF.  The Contractor shall be free to start and stop all primary equipment and incidentals to the heating and air conditioning systems by mutual agreement between the Contractor and the LDWF Maintenance Superintendent or his designee.  The Contractor will furnish a detailed estimate of downtime for all major repairs.

On-Call/Emergency Service

The Contractor will make emergency service available on a continuous twenty-four (24) hour basis for HVAC equipment located at the LDWF Headquarters campus. All work needed to assure a complete, dependable and operational system must be rendered.

The Contractor will provide an itemized invoice to LDWF, which includes work hours, as defined in the list below, and the materials and equipment needed to complete the job. The accepted billing rate will remain in effect during the duration of the contract.

Straight time (7:00am-5:00pm CT Monday-Friday) ----------------- per working hour

Time and one-half (5:01pm-6:59am CT Monday-Thursday) ------- per working hour

Double time (5:01pm CT Friday-6:59am CT Monday & Holidays) ---- per working hour

Note: The working hour rate is defined as the number of hours on site needed to complete the task. Working hour should not be confused with man-hours. LDWF will not be responsible for fuel surcharges or travel time to and/or from the job site.

The Contractor will be contacted by the LDWF Maintenance Superintendent or his designee when a problem has been identified. The Contractor is required to maintain a point of contact for service 24 hours per day, 7 days per week, including holidays.  Response time is not to exceed 2 hours unless a mutual agreement has been made between the Contractor and the LDWF Maintenance Superintendent or his designee

LDWF Campus Check-In and Check-Out Procedures

Normal business hours: If an appointment is scheduled during normal business hours (7:00 a.m. to 4:30 p.m. CT) Monday through Friday, excluding LDWF holidays, the Contractor must report to the lobby of the LDWF main building to check-in and meet with the LDWF Maintenance

Superintendent or his designee. The Contractor must meet again with the LDWF Maintenance Superintendent or his designee once work is complete to perform completion walkthroughs, if necessary. The Contractor must checkout in the lobby of the LDWF main building prior to leaving the campus.

After hours: If appointment is scheduled after hours, the Contractor must make arrangements to meet with the LDWF Maintenance Superintendent or his designee prior to beginning work. The Contractor must meet again with the LDWF Maintenance Superintendent or his designee once work is complete to perform completion walkthroughs, if necessary.

Contractor Qualifications

The Contractor must be a licensed HVAC service contractor and shall have all the necessary licenses required by the city, parish and state to perform the work required by these specifications on the equipment listed in Appendix A to this Attachment B. Service personnel must have at least 5 years of experience on the specified equipment.  Contractor must provide licenses required and service personnel years of experience prior to award.

Warranty Clause

The Contractor will be responsible for providing the manufacturer’s standard warranty on all parts installed and labor performed.

Insurance Requirements

Insurance Requirements for this contract are listed in Attachment A – Special Terms & Conditions of this solicitation. A Certificate of Insurance meeting the listed requirements must be submitted to the Office of State Procurement (OSP) upon request and is a requirement for award.

Written Reports

The Contractor shall provide LDWF personnel with a written report of all work performed for each inspection, repair or emergency call.  The Contractor shall provide an annual inspection checklist of all the equipment listed in Appendix A to this Attachment B. The checklist developed by the Contractor and approved by LDWF, may be submitted in place of the manufacturer’s checklists.

Pre-Bid Jobsite Visit

***This contract requires a Mandatory Pre-Bid Jobsite Visit ***

Please see Attachment A of this solicitation for the mandatory pre-bid jobsite visit requirements.

Appendix A

HVAC Equipment List for LDWF Headquarters Campus

2000 Quail Drive, Baton Rouge, LA  70808

| Manufacturer | Description | Model # | Serial # |
| --- | --- | --- | --- |
| Trane | Series R | RTWD 090F 2A02 A1A1 AA1A 1A1X 1A1A 0000 0000 0000 0001 00D0 | U09D03628 |
| Trane | Series R | RTWD 090F 2E01 A1A1 AA2A 1A1X 1A1A 0000 0000 0000 7001 00D0 | U15L03570 |
| Carrier | Air Cooled Chiller | 30RCA02553102 | 4124Q903084 |
| Trane | Air Cooled Chiller | CGAM-060A-2Z03-AX02-A1A1-A1AX-XA1A-1AXX-XXXX-XA1A-3A10-1XXL-XX | U23L03199 |
| Evapco | Cooling Tower | LSTE-4112 | 16-791339-791344 |
| Evapco | Cooling Tower | LSTE-4112 | 16-791339-791339 |
| Trane | Package Unit/Self Contained | EBC24A4E0B090000000000 00000000000000000 | 22433365JA |
| Trane | Package Unit/Self Contained | EBC24A4E0B0000000000 00000000000000000 | 22433371JA |

| Item | Model # | Serial # / Location |  |
| --- | --- | --- | --- |

| Fan Coil Unit | C-736595 | 5th floor |
| --- | --- | --- |
| Split system | CE3AXA060000A6AA | Serial # 300ZX88147 - Bunkhouse |
| AHU | ITF-BZ21 | Serial # A000762-002-00 – Annex rear |
| AHU | ITF-BZ47 | Serial # A000762001-00 - big unit |
| Boiler | 81-286 | Knight Lochinvar – Annex rear |
| Boiler | CBN0497 | Serial # C11H00231916 – Annex inside |
| Boiler | WGB-2000-6 | Serial # 67-39939 – Equipment Room |
| Package Unit | RRNL-B036JK065 | Serial # 2G7409ADAAF071302514 – Rooftop Lab |
| AHU | LSL117DV | Serial # 3SM00051-04 – 4th floor stairwell |
| AHU | LSL122DV | Serial # 3SM00050-04 – 4th floor near middle hallway |
| AHU | LSL122DV | Serial # 3SM00046-04 – 3rd floor stairwell |
| AHU | LSL122DV | Serial # 3SM00047-04 – 3rd floor near middle hallway |
| AHU | LSL122DV | Serial #3SM00014-04 – 2nd floor stairwell |
| AHU | LSL117DV | Serial # 3SM00048-04 – 2nd floor near middle hallway |
| AHU | LS122DV | Serial # 3SM00044-04 – 1st floor lobby #1 |
| AHU | LSL122DV | Serial # 3SM00045-04 – 1st floor lobby #2 |
| AHU | LSL122DV | Serial # 3SM00043-06 -1st floor licensing |
| AHU | 39MN10W02B56B23XFE | Serial # 2223U36641 – 1st floor trip tickets |
| Air Compressor | N/A | Located in Equipment Room in Chiller Room |

Appendix B

Preventive Maintenance Program for LDWF Headquarters Campus 2000 Quail Drive, Baton Rouge, LA  70808

Preventive Maintenance Program (PMP) including but not limited to Air Handlers, Chillers, Cooling Towers, and VAV/CVB Boxes

## 1.  Purpose

This document is intended for use in a State of Louisiana Competitive Bid / Request for Proposal (RFP) issued under applicable state procurement statutes and regulations. It defines the minimum Preventive Maintenance (PM) scope of work, documentation standards, and performance expectations required for publicly funded facilities.

The scope is written to support transparency, fair competition, and post-award enforceability. All bidders are expected to price and execute the work exactly as described unless a clearly stated exception is submitted in writing.

## 2.  Scope of Work

This scope defines the minimum required services to be included in all bids. Contractors may propose additional services as optional line items but shall not omit or reduce the tasks outlined herein.

This PMP applies to the following systems:

Water-Source Air Handling Units (AHUs)

Chilled Water Systems (Air-Cooled or Water-Cooled Chillers)

Cooling Towers and Condenser Water Systems

Variable Air Volume (VAV) and Constant Volume Box (CVB) Terminal Units

All work shall be performed in accordance with all manufacturer recommendations, American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE) guidelines, and industry best practices.

## 3.  Safety, Compliance & Regulatory Requirements (Mandatory)

All work shall comply with applicable local, state, and federal regulations, including but not limited to: OSHA safety standards, EPA regulations (including refrigerant handling), American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE) guidelines and any applicable state procurement and public-works requirements.

Minimum Safety Requirements:

Lockout/Tagout (LOTO) procedures to be utilized during all site visits.

Appropriate Personal Protective Equipment (PPE) is required at all times.

All chemical handling to be in accordance with all Safety Data Sheets (SDS) requirements.

Confined space and fall protection procedures followed where applicable - Electrical work performed only by qualified personnel.

Failure to comply with all safety minimum requirements may be grounds for contract termination in accordance with State procurement rules and contract terms.

## 4.  Preventive Maintenance Tasks by Equipment Type

### 4.1  Water‑Source Air Handling Units (AHUs)

Inspection & Mechanical

Inspect cabinet, panels, and access doors for damage and/or air leaks.

Inspect and tighten belts.

Inspect pulleys and pulley alignment.

Inspect bearings and lubricate where applicable.

Inspect fan wheel and housing for debris or imbalance.

Airside Components

Inspect filters; if dirty, inform the Building Manager.

Inspect coils for dirt, biological growth, and/or corrosion. Correct and clean as needed.

Clean coils using approved chemicals and methods per the manufacturer’s specifications.

Inspect drain pan and trap. Clean and flush as needed.

Water‑Side Components

Inspect chilled water and heating water control valves.

Check for leaks at piping connections.

Verify for proper actuator operation and valve response

Electrical & Controls

Inspect motor wiring and connections.

Measure and record motor amperage.

Verify safeties and interlocks.

Confirm Building Automation System (BAS) communication and setpoints. Make recommendations regarding appropriate adjustments per requests by occupants.

Documentation

Record supply/return air temperatures.

Record entering/leaving water temperatures.

Capture before/after photos where applicable.

Provide all Documentation in the final report to the Building Manager.

### 4.2  Chillers (Air‑Cooled and Water‑Cooled)

Mechanical Inspection

Inspect compressor(s) for abnormal noise or vibration.

Inspect oil levels (where applicable).

Inspect refrigerant piping for oil residue or leaks.

Heat Exchangers

Inspect evaporator and condenser barrels.

Clean condenser coils or tubes as required.

Verify water flow and pressure drop.

Electrical

Inspect starters, contactors, and control panels.

Tighten electrical connections.

Measure and record compressor amperage and voltage.

Operational Checks

Verify chilled water supply and return temperatures.

Confirm proper staging and unloading.

Verify safeties, alarms, and limit controls.

Controls & Building Automation System (BAS)

Verify setpoints and schedules.

Confirm lead/lag sequencing.

Check sensor accuracy.

Documentation

Record pressures, temperatures, and amperage.

Document any fault history or active alarms and provide in the final inspection report.

### 4.3  Cooling Towers

Structural & Mechanical

Inspect tower casing, louvers, and basin.

Inspect fan blades, gearboxes, and motors.

Verify belt condition or direct‑drive operation.

Grease bearing as needed.

Verify proper operation.

Water System

Inspect basin for debris and biological growth.

Clean strainers and screens.

Verify proper water level and makeup operation.

Chemical Treatment

Verify chemical feed pumps for operation.

Check for scale, corrosion, or algae.

Coordinate with water treatment vendor as needed.

Electrical & Controls

Inspect fan starters and disconnects.

Verify variable frequency drive (VFD) operation (if equipped).

Confirm basin heaters and freeze protection.

Documentation

Record entering and leaving condenser water temperatures.

Record motor amperage.

### 4.4  Variable Air Volume (VAV) and Constant Volume Box (CVB) Boxes

Mechanical

Inspect damper operation and linkage.

Inspect insulation integrity.

Check for air leaks or loose panels

Controls

Verify actuator operation.

Confirm airflow sensor tubing is clear.

Verify box responds to temperature and airflow commands.

Heating Components

Inspect electric or hot water reheat coils.

Verify safeties and control operation.

Inspect wiring and connections.

Operational Checks

Verify minimum and maximum airflow settings.

Confirm zone temperature control

Documentation

Record airflow readings (CFM).

Note zones with comfort complaints

## 5.  PM Frequency

## Semi-Annual Preventive Maintenance (Mandatory)

## 1 Spring visit focused on cooling readiness

1 Fall visit focused on heating readiness

All equipment listed in the asset inventory shall be serviced during each visit unless otherwise approved in writing by the Owner.

## 6.  Reporting, Deficiencies & Compliance

All deficiencies shall be documented and categorized as Routine, Priority, or Critical (Red-Flag).

Critical (Red-Flag) items are defined as conditions presenting immediate risk to safety, equipment integrity, or building operation.

Written notification of Critical items shall be provided to the Owner within 24 hours.

Photo documentation is required for all deficiencies.

Corrective repairs are not included unless separately authorized through State procurement procedures and issued via approved change order or separate solicitation.

## 7.  Required Deliverables

The awarded contractor shall provide the following deliverables suitable for public record retention and audit: Completed PM checklist for each asset, recorded operational readings, photo documentation, and a written summary report following each semi-annual visit.

Incomplete or late documentation may be considered non-performance.

8.  Owner Provided Supplies and Services

The Louisiana Department of Wildlife and Fisheries (LDWF) will provide belts only to the contractor for the contractor to utilize when replacing belts.

LDWF will also provide and change HVAC filters.