**If bidding other than specified, please provide manufacturer’s specs for “or equal” items. **

Scope of Work:

The Contractor shall supply all labor, equipment, and materials to remove and replace the existing generators at 16 different locations for the Department of Public Safety (DPS). Of the 16 sites, 11 shall be indoor skid mounted propane vapor generators. The remaining five will be outdoor enclosure diesel generators. All will require a new 200-amp automatic transfer switch with an outdoor enclosure.

Location:

Radio Maintenance

7919 Independence Blvd

Baton Rouge, LA 70806

Agency Contact:

Paul Dupuis; (225) 573-0535; Paul.Dupuis@la.gov

Reginald Carolina; (225) 603-9022; Reginald.Carolina@la.gov

Specifications:

The Contractor shall be responsible for the following:

200-amp Automatic Transfer Switch (ATS)

The Contractor shall provide and install Automatic Transfer Switches ASCO 300 series or equal with single-phase 200-amp ATS and digital display.

Specify Brand/Model Bidding: ____________________

- Automatic Transfer Switch shall have a built-in load/no load engine exerciser with battery memory backup.

- Automatic Transfer Switch shall have an UL Type 3R (outdoor) enclosure.

- Automatic Transfer Switch shall have strip heaters included.

40KW Indoor Propane Vapor Skid Generators

  - The Contractor shall provide and install Blue Star Model PS40-01 or equal generators, single-phase 240 volts, 60Hz.

Specify Brand/Model Bidding: ____________________

  - The generators shall be permanently bolted to concrete slab inside the building.

  - The generators shall be capable of providing a minimum of 40 Kilowatts of 120/140 volts single phase, 60 Hz electrical power.

  - The generators shall be propane vapor gas operation.

  - The generators shall contain built-in automatic battery charging systems.

  - The exhaust shall be plumbed to the outside of the shelter, with a rainproof exhaust cap.

  - The pad type vibration isolators shall be mounted between the mounting base and pad to reduce noise and transmitted vibrations as supplied by the manufacturer.

  - The generator control panels shall allow automatic remote starting/stopping, precise frequency and voltage regulation, alarm and status message display, output metering, auto-shutdown at fault detection. All software licenses and login credentials shall be supplied to modify parameters within the generator control panel and to perform repairs and maintenance.

  - The generators shall have auxiliary relay contacts for configurable inputs and outputs. All software licenses and login credentials shall be supplied to modify the relays.

  - The generators shall include a jacket water heater -20F 1500-Watt 120 Volt AC.

  - The generators shall be capable of network connectivity for remote control and monitoring.

  - The Contractor shall provide three sets of owner’s manuals specific to the product supplied. The manuals must accompany delivery of the equipment and contain general operating instruction, preventive maintenance, wiring diagrams, schematics and parts exploded views specific to this model.

  - The generators shall include a two year/2000-hour parts and labor warranty.

40KW Outdoor Enclosure Diesel Generator

The Contractor shall provide and install Blue Star Model JD40-03 or equal generators

Specify Brand/Model Bidding: ____________________

- The Contractor shall remove the existing diesel generators from the onsite pad, set it aside on 4x4 treated timber for future retrieval.

  - If it is determined that the existing pad is adequate for the new generator in accordance with the manufacturer’s recommendations, it may be used. If it is not, a new pad shall be constructed by the Contractor.

  - The Contractor shall install the new generators on the pad, securely fastening in accordance with the manufacturer’s instructions.

  - The Contractor shall remove the existing automatic transfer switch and replace it with the one specified.

  - The Contractor shall electrically connect new 40KW generator to the new ATS using proper wire and conduit.

  - The Contractor shall connect the following output and input relays to the customer supplied wiring:

  - Remote start contact closure

  - Common Alarm- Normally open

  - Generator run- Normally open

- The Contractor shall perform complete manufacturer acceptance test and provide copies of all test documents.

General Terms:

- All corrections for work that is unsatisfactory shall be corrected at the vendor’s expense and must be completed satisfactorily before approval and final payment is made.

- All work shall conform to the requirements of all laws and ordinances in force in the locality in which the work is performed.

- The Contractor shall return all areas to existing condition if damaged.

- WARRANTY: The standby electric generating system components, complete engine-generator and instrumentation panel shall be warranted by the manufacturer against defective materials and factory workmanship during the manufacture warranty period. Any defective parts shall be repaired or replaced at the manufacturer's option free of charge for parts, labor and travel. The warranty period shall commence when the standby power system first is placed into service. In the judgment of the specifying authority, the manufacturer supplying the warranty for the complete system must have the necessary financial strength and technical expertise with all components supplied to provide adequate warranty support.

Locations: