Attachment B - Special Terms and Conditions

RFx number: 3000025994

# Contract Title: Emergency Potable Water Storage Container and Supplies Rental - Statewide

# Purpose

In an effort to provide a more efficient use of resources, the Governor’s Office of Homeland Security and Emergency Preparedness (GOHSEP) is seeking providers of onsite rental potable water storage solutions for use during Governor-declared emergency scenarios. Onsite potable water storage will reduce the amount of time that potable water tankers will be tied up on one jobsite and open up the possibility of tankers having the ability to serve multiple delivery locations.

GOHSEP will determine the delivery locations for Potable Water Tank Assemblies as needed. All Potable Water Tank Assemblies provided will be filled, or refilled as needed, by Contractors providing Potable Water Tanker & Transportation Services under separate contracts (T# 92725).

# Emergency Tank Truck Bulk Water Hauling in Louisiana

All bulk water hauling will be directed by the Louisiana Department of Health, Office of Public Health, Safe Drinking Water Program (LDH-OPH-SDWP) under the direction of the Chief Engineer. The State will coordinate with the Public Water System supplying the bulk water and the Contractor(s). All water supplied will be in compliance with the Safe Drinking Water Act and the Louisiana Administrative Code, Title 51 (Sanitary Code). The LDH-OPH-SDWP can be reached at telephone number (225) 342-7499 and is located in the Bienville Building at 628 North 4th Street, Baton Rouge, LA 70802.

Food-grade trucks only are allowed for potable water use.  Tanks previously used to transport petroleum products, toxic materials or other deleterious substances shall not be used to haul potable water.  Drinking water may not be transported or stored in tanks used for any non-food product.

Booster Pump Requirements

All booster pumps must be able to be powered by a generator.

# Requirements for Tank Construction

All tanks—pillow/bladder-style, collapsible, or vertical—shall be constructed with materials that meet NSF/ANSI 61 standards.

Each pillow/bladder/onion tank must be accompanied with a waterproof ground mat, which is longer and wider than the tank, in order to protect and cushion from any ground obstructions.

Pillow/bladder/onion tanks smaller than 1,000 gallons shall be equipped with one 2” Capped Camlock (fill & discharge) and a 2” Capped Camlock with Standpipe (vent).

Pillow/bladder tanks 1,000 gallons or larger shall be equipped with two 2” Capped Camlock (fill & discharge) and a 2” Capped Camlock with Standpipe (vent).

# Cleaning Procedures Prior to Service as a Bulk Water Tank

Tanks that contain potable water regularly from a public water system approved by the Louisiana Safe Drinking Water Program (Department of Health, Office of Public Health (LDH-OPHSDWP) source need not be cleaned between uses, but should be flushed with disinfected water between uses.

Bulk water storage containers used for a food product other than water shall comply with the following cleaning and disinfection procedures.

- For milk trucks and military-style water trucks or trailers, tanks should be scrubbed with  clean water and flushed thoroughly, then inspected for cleanliness including the absence   of particulate matter such as rust and sediment (see page 3 for Confined Space Entry Directions).  A certified milk or juice wash station is recommended, since  	car washes do not provide the needed level of cleanliness.  The certified wash station can also supply a wash sticker to be used as proof of proper washing.

- The following cleaning procedures may be employed for tank trucks/storage containers normally used for hauling/storing such liquids as apple juice, vinegar, wine, yeast, linseed oil, corn syrup, peanut oil, margarine oil, etc.

  - Open the drain and flush with hot water.

  - Steam with an emulsifying detergent until the tank is clear.  Where steam is not  available, circulate the detergent at a temperature of 180 to 210 degrees Fahrenheit, changing the location of the nozzle to keep the interior continuously wet from top to bottom.  Return the solution to the supply tank and re-circulate until clean.

  - Rinse the tank thoroughly with hot water and drain to an approved disposal   facility (see page 3 for Confined Space Entry Directions).

  - Tanks used for transport/storage of dairy products must have the interior of the tank inspected with a black lamp (ultraviolet) after cleaning and flushing as outlined above. Tanks shall not be used when odors or contaminants are found or suspected. Waste chlorine solutions should be disposed of at proper waste disposal sites so that their disposal does not result in fish kills, etc.

- All food grade tanks shall receive an initial wash at a LDH-approved milk tank truck washing facility, and have a current wash sticker.  The location of the nearest approved  milk wash station can be obtained by calling the Milk and Dairy Program at 225-342-

7655.

- The interior of the tanks shall be checked with an organic vapor meter (OVA or HNu)  and an explosive limit meter after cleaning and prior to use.  Any tank with significant  readings shall be rejected.

# Requirements for Cleaning and Sanitizing Auxiliary Equipment

All hoses, connections, pumps, heaters and other water contact equipment shall be cleaned and sanitized with a concentrated solution of chlorine (3 oz. of 5.25 percent household bleach to two (gallons of water) by brushing solution on all exposed parts.  See page 4 for larger volume dosing.

All hoses used for loading and unloading should be stored off the ground at all time and all couplings or water contact surfaces should be covered with caps or plastic coverings to protect them from contamination during storage and transportation.  Hoses should be made of materials which have no influence on the taste or odor of the water and which are approved for potable water use.  Examples are piping made of polyvinyl chloride (PVC), polyethylene (PE), acrylonitrile-butadiene-styrene (ABS) or other equivalent materials.

# Water Source and Quality

Only a water supply which has been permitted or approved by the LDH-OPH Safe Drinking Water Program shall be used as a source to fill containers during water hauling operations. Water tankers may only fill at designated locations approved by the public water system.

LDH will designate one or more public water systems closest to the emergency event that is not operating under a boil advisory to provide the bulk water for the event.

# Confined Space Entry Directions

Caution – Storage tanks are considered confined spaces.  Residual compounds or cleaning compounds which may be introduced can cause a hazardous atmosphere to workers who enter for cleaning purposes. Tank interiors may be extremely slippery.  Minimum entry requirements include:

- Continuous forced ventilation to insure dilution of residual contaminants and to provide sufficient oxygen, and;

- A standby worker attending a lifeline attached to the entry worker(s).  If at all possible, these cleaning procedures should be accomplished without entry.

# Dosages of Chlorinating Compounds for Disinfection

Liquid Sodium Hypochlorite – 5.25 Percent Available Chlorine

(Household Bleach such as Clorox, Purex, Speedup, etc.)

(Manufacturer’s name is for information only and not to show preference)

| Dosage parts per million (ppm) | 50 gallons water | 100 gallons water | 500 gallons water | 1000 gallons water | 5000 gallons water |
| --- | --- | --- | --- | --- | --- |
| 1 | ¾ teaspoon | 1 ½ teaspoons | 7 ½ teaspoons | 3 ounces | 13 ounces |
| 10 | 7 ½ teaspoons | 3 ounces | 12 ounces | 1 ½ pints | 1 gallon |
| 50 | 6 ounces | 13 ounces | 2 quarts | 1 gallon | 4 ¾ gallons |
| 200 | 1 ½ pints | 1 ½ quarts | 2 gallons | 3 ¾ gallons | 19 gallons |

Calcium Hypochlorite Granules or Tablets – 70 Percent Available Chlorine

(HTH, Perchloron, Sentry, etc.)

(Manufacturer’s name is for information only and not to show preferences)

| Dosage parts per million (ppm) | 50 gallons water | 100 gallons water | 500 gallons water | 1000 gallons water | 5000 gallons water |
| --- | --- | --- | --- | --- | --- |
| 1 | - | - | - | - | 1 ounce |
| 10 | - | - | 1 ounce | 2 ounces | 10 gallons |
| 50 | - | 1 ounce | 5 ounces | 10 ounces | 3 pounds |
| 200 | 2 ounces | 4 ounces | 1 pound & 3 ounces | 2 pounds & 6 ounces | 12 pounds |