# Line 1 800KW Generator

Diesel Standby Generator – Blue Star Power Systems model MD8000-01 or Equal

General

Furnish one diesel standby generator system suitable for outdoor installation and emergency standby service. Equipment shall be Blue Star Power Systems Model MD800-01 or equal, meeting or exceeding all requirements specified herein.

Specify Brand Bidding: ______________

Specify Model Bidding: ______________

Specify Delivery Days ARO Bidding: ____________________

__________________________________________________________________________________

# Generator System Component

The generator system shall include the following:

- Two-year standard manufacturer warranty

- Battery system complete with rack, cables, and battery charger

- Engine safety shutdowns and generator metering

- Mainline circuit breaker, factory mounted, rated 1,200 amps

- Engine block heaters, quantity two, rated 9,000 watts each at 240 volts

- Remote annunciator

- Must be an Aluminum weather-protective housing with critical-type exhaust, stainless steel flexible exhaust connector, and rain cap

- Enclosure wind rated to 200 MPH

- 3,600-gallon double-wall UL 142 listed sub-base fuel tank, complete with leak detection alarm and low fuel level contacts

- Fuel tank sized to provide 48 hours of operation at full load

- Initial oil and antifreeze supplied

- Field testing and complete system checkout prior to acceptance

Specify Manufacturer Warranty Bidding: ____________________

Specify Bidding Battery System Complete with Rack, Cables, and Battery Charger: Yes____ No____

Specify Bidding Engine Safety Shutdowns and Generator Metering: Yes____ No____

Specify Mainline Circuit Breaker Rating Bidding: ____________________

Specify Engine Block Heater Quantity Bidding: ____________________

Specify Engine Block Heater Rating Bidding: ____________________

Specify Bidding Remote Annunciator: Yes____ No____

Specify Bidding Aluminum Weather-Protective Housing with Critical-Type Exhaust, Stainless Steel Flexible Exhaust Connector, and Rain Cap: Yes____ No____

Specify Enclosure Wind Rating Bidding: ____________________

Specify Fuel Tank Capacity Bidding: ____________________

Specify Bidding Double-Wall UL 142 Listed Sub-Base Fuel Tank with Leak Detection Alarm and Low Fuel Level Contacts: Yes____ No____

Specify Bidding Fuel Tank Sized for 48 Hours Operation at Full Load: Yes____ No____

Specify Bidding Initial Oil and Antifreeze Supplied: Yes____ No____
__________________________________________________________________________________

# Generator Rating

- Standby Rating: 800 kWe

- Voltage: 480/277 VAC

- Phase: 3-phase

- Frequency: 60 Hz

- Speed: 1800 RPM

- Power Factor: 0.8

- Full Load Current: Minimum 1,204 Amps

- Connection: 12-lead wye

- Temperature Rise: Maximum 125°C / 40°C

Specify Standby Rating Bidding: ____________________

Specify Voltage Bidding: ____________________

Specify Phase Bidding: ____________________

Specify Frequency Bidding: ____________________

Specify Speed Bidding: ____________________

Specify Power Factor Bidding: ____________________

Specify Full Load Current Bidding: ____________________

Specify Connection Type Bidding: ____________________

Specify Temperature Rise Bidding: ____________________
__________________________________________________________________________________

# Engine

- Diesel engine, 12-cylinder V configuration, or equal

- 4-cycle, turbocharged, aftercooled

- Rated for standby service at 1800 RPM

- Manufacturer: Mitsubishi or equal

- Engine shall be compliant with applicable EPA emissions regulations

Specify Engine Type and Configuration Bidding: ____________________

Specify Bidding 4-Cycle Turbocharged Aftercooled Engine: Yes____ No____

Specify Engine Speed Rating Bidding: ____________________

Specify Manufacturer Bidding: ____________________

Specify Bidding Engine Compliant with Applicable EPA Emissions Regulations: Yes____ No____
__________________________________________________________________________________

# Generator

- Brushless, rotating field alternator

- Automatic Voltage Regulator (AVR)

- Voltage regulation: ±0.5%

- Suitable for 100% rated load in one step

- Harmonic distortion not to exceed 5%

- Compliant with NEMA MG-1, IEEE, and ANSI standards

Specify Bidding Brushless Rotating Field Alternator: Yes____ No____

Specify Bidding Automatic Voltage Regulator: Yes____ No____

Specify Voltage Regulation Bidding: ____________________

Specify Bidding Suitable for 100% Rated Load in One Step: Yes____ No____

Specify Harmonic Distortion Bidding: ____________________

Specify Bidding Compliant with NEMA MG-1, IEEE, and ANSI Standards: Yes____ No____
__________________________________________________________________________________

# Controls

- Provide a microprocessor-based digital control panel, DCP7310 or equal, including:

- Digital AC metering (voltage, current, frequency, kW)

- Engine monitoring and protection

- Generator protection functions

- Event and fault logging

- CAN Bus (J1939) engine communications

- RS-485 communication interface

- Capable of remote monitoring and annunciation

Specify Control Panel Model Bidding: ____________________

Specify Bidding Digital AC Metering for Voltage, Current, Frequency, and kW: Yes____ No____

Specify Bidding Engine Monitoring and Protection: Yes____ No____

Specify Bidding Generator Protection Functions: Yes____ No____

Specify Bidding Event and Fault Logging: Yes____ No____

Specify Bidding CAN Bus J1939 Engine Communications: Yes____ No____

Specify Bidding RS-485 Communication Interface: Yes____ No____

Specify Bidding Capable of Remote Monitoring and Annunciation: Yes____ No____
__________________________________________________________________________________

# Enclosure

- Type: Level 1 weatherproof enclosure (UL 142)

- Suitable for continuous outdoor operation

- Wind Rating: Minimum 200 MPH

- Compliant with IBC 2021 and ASCE 7-16

- Sound Level: Not to exceed 83 dBA at full rated load, measured at 23 feet

Specify Enclosure Type Bidding: ____________________

Specify Bidding Suitable for Continuous Outdoor Operation: Yes____ No____

Specify Wind Rating Bidding: ____________________

Specify Bidding Compliant with IBC 2021 and ASCE 7-16: Yes____ No____

Specify Sound Level Bidding: ____________________
__________________________________________________________________________________

# Fuel System

- Integral base-mounted fuel tank

- Construction: Double-wall, UL 142 listed

- Capacity: Minimum 3,600 gallons

- Runtime: Minimum 48 hours at rated standby load

Specify Bidding Integral Base-Mounted Fuel Tank: Yes____ No____

Specify Bidding Double-Wall UL 142 Listed Construction: Yes____ No____

Specify Fuel Tank Capacity Bidding: ____________________

Specify Runtime Bidding: ____________________
_________________________________________________________________________________

# Standards & Codes

Generator system shall comply with all applicable standards, including but not limited to:

- NFPA 110 (Level 1) Emergency Power Supply Systems

- NEC - NATIONAL ELECTRIC CODE

- EPA emissions requirements – EPA Certified Tier 2 (DEF) FEDERAL GUIDELINE

- Applicable UL and/or CSA listings for electrical components

- All State and local codes and regulations

Specify Bidding NFPA 110 Level 1 Emergency Power Supply Systems: Yes____ No____

Specify Bidding NEC National Electric Code Compliance: Yes____ No____

Specify Bidding EPA Certified Tier 2 DEF Federal Guideline: Yes____ No____

Specify Bidding Applicable UL and/or CSA Listings for Electrical Components: Yes____ No____

Specify Bidding Compliance with All State and Local Codes and Regulations: Yes____ No____

__________________________________________________________________________________

# Warranty

- Provide minimum 2-year / 2,000-hour standby warranty covering generator, engine, and alternator.

Specify Warranty Term Bidding: ____________________

Specify Bidding Warranty Covers Generator, Engine, and Alternator: Yes____ No____

__________________________________________________________________________________

# Approved Equal Requirements

Proposed equal equipment must:

- Meet or exceed all listed requirements

- Be factory-assembled and factory-tested

# Line 2: 300KW Generator

Diesel Standby Generator – Blue Star Power Systems model PD300-01 or Equal Specification

General

Furnish one diesel standby generator system suitable for outdoor installation and emergency standby service. Equipment shall be Blue Star Power Systems Model PD300-01 or equal, meeting or exceeding all requirements specified herein.

Specify Brand Bidding: ______________

Specify Model Bidding: ______________

Specify Delivery Days ARO Bidding: ____________________

__________________________________________________________________________________

# Base Bid - Generator System Component

The generator system shall include the following:

- Two-year standard manufacturer warranty

- Battery system complete with rack, cables, and battery charger

- Engine safety shutdowns and generator metering

- Mainline circuit breaker, factory mounted, rated 450 amps

- Engine block heater, rated 2,000 watts at 240 volts

- Remote annunciator

- Must be an Aluminum weather-protective housing with critical-type exhaust, stainless steel flexible exhaust connector, and rain cap

- Enclosure wind rated to 200 MPH

- 1,620-gallon double-wall UL 142 listed sub-base fuel tank, complete with leak detection alarm and low fuel level contacts

- Fuel tank sized to provide 72 hours of operation at full load

- Initial oil and antifreeze supplied

- Field testing and complete system checkout prior to acceptance

Specify Manufacturer Warranty Bidding: ____________________

Specify Bidding Battery System Complete with Rack, Cables, and Battery Charger: Yes____ No____

Specify Bidding Engine Safety Shutdowns and Generator Metering: Yes____ No____

Specify Mainline Circuit Breaker Rating Bidding: ____________________

Specify Engine Block Heater Rating Bidding: ____________________

Specify Bidding Remote Annunciator: Yes____ No____

Specify Bidding Aluminum Weather-Protective Housing with Critical-Type Exhaust, Stainless Steel Flexible Exhaust Connector, and Rain Cap: Yes____ No____

Specify Enclosure Wind Rating Bidding: ____________________

Specify Fuel Tank Capacity Bidding: ____________________

Specify Bidding Double-Wall UL 142 Listed Sub-Base Fuel Tank with Leak Detection Alarm and Low Fuel Level Contacts: Yes____ No____

Specify Runtime Bidding: ____________________

Specify Bidding Initial Oil and Antifreeze Supplied: Yes____ No____

__________________________________________________________________________________

# Generator Rating

- Standby Rating: 300 kWe

- Voltage: 480/277 VAC

- Phase: 3-phase

- Frequency: 60 Hz

- Speed: 1800 RPM

- Power Factor: 0.8

- Full Load Current: 452 Amps

- Connection: 12-lead wye

- Temperature Rise: 125°C / 40°C

Specify Standby Rating Bidding: ____________________

Specify Voltage Bidding: ____________________

Specify Phase Bidding: ____________________

Specify Frequency Bidding: ____________________

Specify Speed Bidding: ____________________

Specify Power Factor Bidding: ____________________

Specify Full Load Current Bidding: ____________________

Specify Connection Type Bidding: ____________________

Specify Temperature Rise Bidding: ____________________

__________________________________________________________________________________

# Engine

- Diesel engine, 6-cylinder inline, or equal

- 4-cycle, turbocharged, charge-air cooled

- Rated for standby service at 1800 RPM

- Perkins 1706D-E93TAG2 or equal

- Engine shall comply with applicable EPA emissions regulations

Specify Engine Type and Configuration Bidding: ____________________

Specify Bidding 4-Cycle Turbocharged Charge-Air Cooled Engine: Yes____ No____

Specify Engine Speed Rating Bidding: ____________________

Specify Manufacturer and Model Bidding: ____________________

Specify Bidding Engine Compliant with Applicable EPA Emissions Regulations: Yes____ No____

__________________________________________________________________________________

# Generator

- Brushless, single-bearing alternator

- Rotating field design

- Automatic Voltage Regulator (AVR)

- Voltage regulation: ±0.5%

- Capable of accepting 100% rated load in one step

- Total harmonic distortion not to exceed 5%

- Compliant with NEMA MG-1, IEEE, and ANSI standards

Specify Bidding Brushless Single-Bearing Alternator: Yes____ No____

Specify Bidding Rotating Field Design: Yes____ No____

Specify Bidding Automatic Voltage Regulator: Yes____ No____

Specify Voltage Regulation Bidding: ____________________

Specify Bidding Capable of Accepting 100% Rated Load in One Step: Yes____ No____

Specify Harmonic Distortion Bidding: ____________________

Specify Bidding Compliant with NEMA MG-1, IEEE, and ANSI Standards: Yes____ No____

__________________________________________________________________________________

# Controls

- Provide a microprocessor-based digital control panel, DCP7310 or equal, including:

- Digital AC metering

- Engine and generator protection

- Event and fault recording

- CAN Bus (J1939) ECU communications

- RS-485 communication interface

- Capable of remote monitoring and annunciation

Specify Control Panel Model Bidding: ____________________

Specify Bidding Digital AC Metering: Yes____ No____

Specify Bidding Engine and Generator Protection: Yes____ No____

Specify Bidding Event and Fault Recording: Yes____ No____

Specify Bidding CAN Bus J1939 ECU Communications: Yes____ No____

Specify Bidding RS-485 Communication Interface: Yes____ No____

Specify Bidding Capable of Remote Monitoring and Annunciation: Yes____ No____

__________________________________________________________________________________

# Enclosure

- Type: Level 1 weatherproof enclosure

- Suitable for continuous outdoor installation

- Wind Rating: Minimum 200 MPH

- Compliant with IBC 2021 and ASCE 7-16

- Sound Level: Not to exceed 85 dBA at full rated load, measured at 23 feet

Specify Enclosure Type Bidding: ____________________

Specify Bidding Suitable for Continuous Outdoor Installation: Yes____ No____

Specify Wind Rating Bidding: ____________________

Specify Bidding Compliant with IBC 2021 and ASCE 7-16: Yes____ No____

Specify Sound Level  Bidding: ________________

__________________________________________________________________________________

# Fuel System

- Integral base-mounted UL 142 fuel tank

- Capacity: 72-hour runtime

- Fuel Volume: 1,620 gallons

Specify Bidding Integral Base-Mounted UL 142 Fuel Tank: Yes____ No____

Specify Runtime Bidding: ____________________

Specify Fuel Volume Bidding: ____________________

__________________________________________________________________________________

# Standards & Codes

- NFPA 110 (Level 1) Emergency Power Supply Systems

- NEC - NATIONAL ELECTRIC CODE

- EPA emissions requirements – EPA Certified Tier 2 (DEF) FEDERAL GUIDELINE

- Applicable UL and/or CSA listings for electrical components

- All State and local codes and regulations

Specify Bidding NFPA 110 Level 1 Emergency Power Supply Systems: Yes____ No____

Specify Bidding NEC National Electric Code Compliance: Yes____ No____

Specify Bidding EPA Certified Tier 2 DEF Federal Guideline: Yes____ No____

Specify Bidding Applicable UL and/or CSA Listings for Electrical Components: Yes____ No____

Specify Bidding Compliance with All State and Local Codes and Regulations: Yes____ No____

__________________________________________________________________________________

# Warranty

Provide minimum 2-year / 2,000-hour standby warranty covering generator, engine, and alternator.

Specify Warranty Term Bidding: ____________________

Specify Bidding Warranty Covers Generator, Engine, and Alternator: Yes____ No____

__________________________________________________________________________________

# Approved Equal Requirements

Proposed equal equipment must:

- Meet or exceed all listed requirements

- Be factory-assembled and factory-tested