State of Louisiana

Office of State Procurement

Jeff Landry

Governor

Taylor F. Barras

Commissioner of Administration

Division of Administration

1201 N. Third Street, Suite 2-160

Baton Rouge, Louisiana 70802-5243

Phone (225) 342-8010

Fax (225) 342-9756

April 21, 2026

Addendum No. 01

Your reference is directed to RFx Number 3000026025 for the Invitation to Bid (ITB) for the State of Louisiana – Generators Towable and Stationary - Statewide, which is currently scheduled to open at 10:00 AM CT on April 28, 2026.

The following are the Vendor’s Inquiries received by the deadline date of April 14, 2026, and the State’s Responses:

Vendor’s Inquiry #1:  UL 2200 Compliance - Listing Requirement - As UL 2200 (ANSI/CAN/UL/ULC 2200) 3rd Edition became mandatory on March 31, 2026, for stationary generator assemblies (Lines 10-173), please confirm whether the State intends to require that all applicable standby generator units be UL 2200 3rd Edition listed assemblies by a recognized testing laboratory.

State’s Response #1: Yes, please see revised Attachment B – Generator Specifications (revised per Addendum No.1 dated April 21, 2026).

Attachment B, Page 3, Unit Performance currently reads: The unit shall be in compliance with UL2200, listed unit frequency regulation and shall not exceed 3 Hz from no load to rated load. Voltage regulation shall be within plus or minus 2% of rated voltage, from no load to full rated load. The instantaneous dip shall be less than 25% of rated voltage unless otherwise specified when full three phase load and rated power factor is applied to the alternator. Recovery to stable operation shall occur within two seconds. Stable or steady state operation is defined as operation with terminal voltage remaining constant within plus or minus 1% rated voltage. A rheostat shall be provided, a minimum plus or minus 5% voltage adjustment from rated value. Temperature rise shall be within NEMA mg-22.40 definition. The rating of the prime mover shall be such that any over-loads which occur during motor starting, even though they may exceed the steady state capability of the prime mover, shall not cause stalling.

Attachment B, Page 3, Unit Performance changed to read: The engine generator assembly shall be listed and labeled to UL 2200 3rd Edition.

All else remains as on original Invitation to Bid.

This addendum is hereby officially made a part of the referenced solicitation.

Acknowledgement: If you have already submitted your bid and this Addendum does not cause you to revise your bid, you should acknowledge receipt of this Addendum by identifying your business name and by signing where indicated.  You may return this Acknowledgement by mail or delivery by hand or courier to: Office of State Procurement, 1201 N. 3rd Street, Ste. 2-160, Baton Rouge, LA  70802, or by fax to: (225) 342-9756.  The State reserves the right to request a completed Acknowledgement at any time.  Failure to execute an Acknowledgement shall not relieve the bidder from complying with the terms of its bid.

Addendum Acknowledged/No changes:

For:  ________________________  By:  __________________________

Revision: If you have already submitted your bid and this Addendum requires you to revise your bid, you must indicate any change(s) below, identify your business name and sign where shown.  Revisions shall be delivered prior to bid opening by mail or delivery by hand or courier to: Office of State Procurement, 1201 N. 3rd Street, Ste. 2-160, Baton Rouge, LA  70802, or by fax to: (225) 342-9756, and indicate the RFx number and the bid opening date and time on the outside of the envelope for proper identification.  Electronic transmissions other than by fax are not being accepted at this time.

Revisions received after bid opening shall not be considered and you shall be held to your original bid.

Revision:

For:  ________________________  By:  __________________________

By:	Donald Hunter

Office of State Procurement

Telephone No. 225-342-5484

Email:  donald.hunter2@la.gov