**If bidding other than specified, please provide manufacturer’s specs for “or equal” items. **

Scope of Work:

The Contractor shall furnish all labor, commercial grade materials, tools, and equipment necessary to remove and replace the Freezer/Cooler at the Camp Minden Dining Facility for the Department of Military Affairs (DMA).

Location:

Camp Minden Dining Facility

100 Louisiana Blvd

Minden LA 71055

DMA Contact:

Darren Thomas

(318) 450-7536

darren.k.thomas.mil@army.mil

Specifications:

The Contractor shall be responsible for the following:

Refrigeration System

- Brand/Model: Mini-Pak MPL-3CZ or Equal

Specify Brand/Model Bidding: ___________________

- The entire unit shall be weather-proofed and a minimum of two coats of paint shall be applied to make the unit rust-proof.

- The unit shall be provided with multi-circuited air-cooled condenser for cooler, freezer and ice machines. The suction line for the low temperature unit must be insulated with Armaflex.

Refrigeration units

- Crankcase heater units shall be provided with every crankcase connection.

- Air-cooled condensing units shall be semi-hermetic compressor, hermetic, or glacier scroll type (Copeland). Each unit shall be equipped with high-low pressure control, liquid line drier, sight glass, suction and discharge vibration eliminator, and head pressure control.

- All compressor units shall be new, and factory assembled to operate with the refrigerant specified in the engineering summary.

Pre-piping

- All copper tubing shall be refrigerant grade A.C.R. or type “L”.

- All refrigerant lines shall be securely supported and anchored with clamps.

- All tubing shall be extended in a neat and orderly manner.

- Silver solder and/or SIL-FOS shall be used for all refrigerant piping. Soft solder is not acceptable.

- All piping of the system shall be leak tested with nitrogen at 300 psi, after the condensing unit and coil has been connected, with the balance of all valves open.

- In the freezer, the unheated drain line must be outside of freezer wall to prevent freezing. Trap drain line outside of freezer.

- The Contractor to provide individual drain line for each evaporator unless otherwise called for.

- All plumbing installation shall be in accordance with local codes.

Control Package

- The package shall have factory mounted and pre-wired control panel complete with interlocked main disconnect, compressor circuit breakers, contactors and time clocks wired for single point power connection.

- The Contractor shall provide and install main fused disconnect, defrost heater between the defrost clock and the refrigeration lines to panel, and use wire harness with wiring for control and local codes.

General Information:

- The Contractor shall be responsible for field verifying all dimensions and existing site conditions of work to be performed. The Contractor shall inspect and verify information provided herein on existing materials and equipment, etc. is correct and inform Project Manager (PM) of any errors or questions prior to commencement of work.

- The Contractor shall take all precautions necessary to prevent damages when delivering materials to site and provide covering to prevent rusting.

- The Contractor shall secure the building, and any sensitive items at the end of each workday in accordance with the designated unit POC.

- The Contractor shall take all necessary precautions to prevent damages during repairs, to include movement and parking of equipment on grass, other improved, or unimproved areas surrounding site.

- All work must comply with all applicable State and Local Safety and Environmental requirements. Occupational Safety and Health Administration (OSHA), National Electrical Code (NEC), Parish, City and State regulation shall be required. The Contractor shall supply all employees with PPE.

- The Contractor must call LA 1-Call and all utility companies prior to digging.

- Hours of operation Tuesday- Friday, 7:00 AM to 5:30 PM and closed on all recognized state and federal holidays.

- The Contractor shall be responsible to provide storage containers. If an onsite storage area is required, the contractor must confirm a storage location for any materials, fixtures, equipment, trailers, etc. stored on site during the term length of the contract. The location will be approved by the Project Manager during the pre- construction meeting.

- The Contractor shall confirm a storage location for all materials stored on site during the term length of the contract. The location shall be approved by the Project Manager prior to delivering.

- The Contractor shall contact, prior to mobilization and demobilization, facility point of contact which will be provided herein.

- The Contractor is responsible for disposal and storage of all materials being removed or installed throughout the project.

- The Contractor shall provide a construction work schedule (Gnant like) 48 hours prior to start of work detailing each task of work.

- All specification sheets and submittals must be pre-approved by the Project Manager prior to ordering.

- The Contractor shall warranty their workmanship and the completed project for a one-year period. One year period starts the date of the filing of the certificate of completion.

- The Contractor shall provide all associated warranty documents to the Project Manager upon completion and final payment.

- Weather days are included in the contract time.

- Work shall be completed in a two-week timeframe and the Contractor must provide a refer trailer for freezer/cooler products.