Attachment B –Specifications

(As Revised Per Addendum #2 released May 8, 2026)

RFx: 3000026122

Generator Preventive Maintenance – Louisiana   Department of Wildlife and Fisheries (LDWF)

SCOPE OF WORK/SERVICES

The scope of work/services required under the terms of this contract include, but not limited to the inspection and testing of generators located at various locations within the state as described on the attached Exhibit "A". Also included under the terms of this contract is generator repair related services.

The entire list of generators (Attachment C – Price Sheet) shall have one major (annual) and one minor inspection and testing each year. Generator maintenance services are to be performed twice a year: one Major Annual (annual) inspection and one minor inspection and testing during course of year. The State reserves the right to cancel the need for the minor inspection if a funding problem develops. The State reserves the right to add and/or delete generators that come into and out of service as need be this contract period.

The vendor must provide services in accordance with the manufacturer’s recommended maintenance schedule.

It is the bidder's responsibility to visit and evaluate each location in order to bid accordingly.

The State is requesting a "turnkey" operation. The expression "turnkey" shall include, but may not be limited to all labor, materials, equipment, fuel, transportation, storage of equipment, insurance, licenses, etc... Required to provide the two needed inspections/testing’s per year.

IMPORTANT NOTICE TO ALL BIDDERS

LICENSES/PERMITS REQUIRED

- A State of Louisiana Electrical License -shall be required for all as provided in LSA R.S. 37:2150 et seq.

- The Contractor shall submit his Louisiana Sales tax License and current occupational license to show he is domiciled and licensed to do business within the State of Louisiana.

- Work under this contract can be described as a preventative maintenance/service and repair contract. The State shall not be restricted from utilizing its own personnel and equipment to perform work associated/included under the terms of this contract.

- Quantities listed for labor related items of work have been estimated and are for bidding purposes only. Actual quantities may be more or less than the estimated bid quantities.

PERMISSIBLE WORKING HOURS/PERIODS

The generators are located in various areas throughout the state. Work shall be scheduled between 7:00 a.m. and 5:00 p.m. Monday through Friday with the exception of transfer switch load testing. Transfer switch load testing shall be scheduled with a LDWF representative and shall be completed in such a manner as not to interrupt the normal operations of the Site. All work shall be scheduled at the States convenience and in cooperation with LDWF representative. The Contractor shall provide priority to LDWF on all scheduled repairs. In the event that the Contractor wishes to work weekends, holidays or outside permissible working periods, the Contractor must secure permission from LDWF Facilities Maintenance Section, and provide at least 72 hours of notification of intentions. The Contractor must also be aware of any local events that may impact his scheduled operation and may be required to alter his schedule accordingly. This modification to the schedule will not be grounds for any additional cost/compensation. This condition applies primarily for generator repair related services.

REPORTS

The Contractor shall provide report sheets to LDWF recording all activities related to the contract to the attention of the listed contact person on the price list.  If reports are not submitted on a timely basis, payment of contractor's invoices may be delayed until proper report is submitted. Reports should accompany The contractor's invoices.

## TECHNICAL SPECIFICATIONS

INSPECTIONS AND  TESTINGS

The Minor inspection and testing shall be performed in October-November timeframe. The Major inspection shall be performed in March-April after award. The process for major and minor service shall repeat itself all years and renewal years thereafter. The State of Louisiana reserves the right to cancel the need for the minor inspection, if a funding a problem develops. The State of Louisiana reserves the right to add and/or delete generators that come into and out of service as need be and adjust unit cost accordingly during this contract period.

Refer to Attachment C – Price Sheet for list of generator sizes (KW ratings) and their respective locations.  It is the bidder's responsibility to evaluate each generator (and types) and bid accordingly.

Exhibit "A" shall be used to indicate the required level of inspection, maintenance and testing. For all inspections, maintenance and testing task, The Contractor must note condition found, condition left and any action taken and recommended.

Exhibits A & B lists the requirements to be completed on an annual basis which includes completing all items in both Exhibit "A" and Exhibit ”B”.  Exhibit "A" lists the requirements for the minor inspection; Exhibit "B" lists the requirements for the major inspection.

Copies of all test results and reports shall be sent to LDWF Facilities Maintenance Section no later than 30 days after completion of service work on all generators. Test results and reports should be sent to the attention of the listed contact person on the price list

MINOR INSPECTION/MAINTENANCE

The Minor inspection and testing shall be performed in October-November timeframe. Minor service maintenance/inspections to each generator listed in Attachment C - Price Sheet shall consist of all labor and materials necessary to perform the minor service one time per year, as per requirements dictated in Exhibit "A" and the replacement of parts/equipment listed below. The State of Louisiana reserves the right to cancel the need for these services, if a funding problem develops.

Payments for Minor inspection shall be submitted to LDWF Facilities Maintenance Section for review/comment and approval along with completed reports for review. Payments for Minor inspection should be sent to the attention of the listed contact person on the price list.

MEASUREMENT AND PAYMENT

Payment for these services will be measured per Lump Sum (one time per year) and shall cover the maintenance service (inspection/testing) specified below for all Generators in Attachment C - Price Sheet of various types, KW ratings and sizes. Minor service maintenance to each generator shall include all labor, equipment, materials and incidentals necessary to accomplish the work.   Also included under these bid items is the following:

  - Oil - (Replace as need be)

  - Lubricant - (Lubricate as need be)

  - Antifreeze - (add as need be)

  - Belts - (Check for cracks/wear and tear)

Exhibit “A”

Minor Periodic Maintenance performed once every 12 months.

Disable Unit from automatically operating for safety purposes.

Provide Minor Annual preventative maintenance for 25 generators listed below.  Total cost shall be inclusive of this service for all generators and shall include travel and labor expenses.

The Contractor shall perform Minor Annual servicing in accordance with the manufacturer's specifications and at a minimum, shall include the following tasks:

1.  Check battery voltage

2.  Check coolant level and coolant condition

3.  Check and replace, as necessary, the oil, air and fuel filters; at a minimum they should be replaced annually.

4.  Open normal source breaker at ATS

5.  Verify the generator starts, ATS transfer to emergency and power to the load is restored.

6.  Allow the generator to run for 30 minutes and note any perceived problems.

7.  Check gauges and meters and record the readings, including the fuel level.

8.  Close normal source breaker at ATS

9.  Verify the ATS transfers to normal

10. Verify proper generator shut down

11. Submit an Annual report that summarizes gauge and meter readings, fuel levels and other problems detected.

12. Record running time in hours

13. Exercise the unit

14. Check for excessive vibration

15. Record housing condition

16. Record coolant temperature

17. Record oil pressure

18. Inspect for oil leaks

19. Inspect belts for wear or damage and note accordingly.

20. Inspect and tighten all bolts

21. Inspect choke

22. Inspect ignition wiring

23. Inspect crankcase breather

24. Check oil level and top off

25. Inspect all filters

26. Lubricate governor and linkage

27. Record coolant protection temperature

28. Check for coolant leaks

29. Inspect hoses and tighten clamps

30. Verify louver operation

31. Check operation of block heater

32. Visually inspect exhaust system silencer

33. Drain all exhaust silencer condensate

34. Visually observe exhaust emissions and record any abnormalities

35. Visually inspect exhaust system connections and ensure that exhaust pipe flappers are properly functioning

36. Check fuel level

37. Compare fuel level indicator with actual fuel level

38. Check day tank float

39. Check fuel transfer pump operation

40. Check operation of solenoid

41. Check all electrical connections

42. Inspect alternator terminals

43. Confirm and record alternator output

44. Inspect and clean all battery terminals

45. Record all charger output

46. Check fluid levels in all batteries

47. Record all battery volts and amps

48. Record all battery specific gravity for each cell of each battery

49. Clean coolant system annually by manufacturer's specifications

NOTE:  (A) After performing item #2, if it is determined that coolant must be changed; coolant can be billed at time of change.

(B) For item #5, with coordination with each facility, ATS transfer to emergency power can be conducted during normal business hours at all sites.

MAJOR INSPECTION/TESTINGS

The Major inspection shall be performed in March-April after award. Major Service maintenance to each generator listed on Attachment C – Price Sheet shall consist of all labor and materials necessary to perform the Major (annual) service once a year, as per requirements dictated in Exhibit A and B and the replacement of parts/equipment listed below. This shall include maintenance to the engine, generator end, remote alarm test, and operational tests further delineated in Exhibits A & B.

Transfer switch testing shall be scheduled through LDWF Facilities Maintenance Section representative to ensure certain critical loads are not interrupted. Terminate transfer test and check operation and timing of re-transfer delay, program transition times and cool down times. Concurrence of any adjustment shall be obtained prior to any adjustment

Payment for Major Annual Maintenance shall be submitted to the State of Louisiana for review/comment and approval along with completed report.

MEASUREMENT AND PAYMENT

Payment for these services will be measured per Lump Sum (one time per year) and shall cover the maintenance service (inspection/testing) specified below for all Generators  and shall cover the annual services (inspections/testing) specified in Exhibits A & B for all generators In Attachment C - Price Sheet  of various types, KW ratings and sizes. Major Service maintenance to each generator shall include all labor, equipment and materials and incidentals necessary to accomplish the work. Also included under this bid item is the following:

    - Filters -- (Replace oil, fuel and air filters) at all major annual services.

    - Oil -- (Replace at all major annual services)

    - Antifreeze Analysis – Send sample for testing- results to be provide to attention of the listed contact person on the price list at the Department of Wildlife and Fisheries.

  - Oil Analysis – Send sample for testing- results to be provide to attention of the listed contact person on the price list at the Department of Wildlife and Fisheries.

  - Fuel Analysis – Send sample for testing- results to be provide to attention of the listed contact person on the price list at the Department of Wildlife and Fisheries.

EXHIBIT B

Major Annual Maintenance performed once every 12 months.

Includes all items in Exhibit A

Provide Major (Line 2) Annual preventative maintenance plus all items listed on Minor (Line 1) Annual preventative maintenance for 25 generators listed below.  Total cost shall be inclusive of this service for all generators quarterly and shall include travel and labor expenses.

The Contractor shall perform Major Annual servicing in accordance with the manufacturer's specifications and at a minimum, shall include the following tasks:

1.  Replace filters (oil, fuel and air) per manufacturer's specifications

2.  Perform 5 minute no -load operational run of the unit looking for any post service problems

3.  Verify integrity of frame ground and re-torque hardware to specifications.

4.  Check generator external and conduit entry condition

5.  Inspect condition of leads and terminal/lug

6.  Check conditions of brushes, slip rings, condition and tightness if applicable

7.  Lubricate generator bearings per manufacturer's specifications.

8.  Perform below Remote Alarm Test:

- perform remote alarms annunciate

- Generator Running

- Generator Over-crank shutdown

- Generator over-speed shutdown

- Generator Low Oil Pressure Shutdown

- Generator High Coolant Temp Shutdown

- Generator Low Coolant Temperature

- Generator Low Coolant Level Shutdown

- Generator Main Tank Low Fuel

- Generator Crank Battery Charge Fail

- Generator Not in Automatic

9. Perform below Operational Test with Load Transfer

- Obtain permission from company representative to perform site-load transfer test

- Check transfer switch operation and position

- Check auto-start system

- Confirm the ATS ON EMERGENCY alarm annunciates

- Check engine instruments

- Check engine instruments

- Check voltage and frequency, and load

- Contractor to load test the Generator for 2 hours:  25% load for the first 30 minutes, 50% for the second 30 minutes, 100% for the last hour.  Contractor to record Hz, Amps, Temp, Freq, every 15 minutes.

- Do not perform a load bank test on generators below 100KW.

*Terminate transfer test and check operation and timing of re-transfer delay, program transition times and cool down times. Obtain concurrence from company representative before adjusting.

HOURLY REPAIRS RELATED SERVICES

Repair related services which are not part of the scope of work specified for major and minor maintenance related services (inspections and testing} shall be performed by a Louisiana licensed electrician and/or certified Generator Technician-Mechanic (as necessary).   All electrical work shall be performed by a State of Louisiana licensed electrician as provided in LSA R. S. 37:2150 et seq.

- Payment for this work is to be made on an hourly basis and shall include all incidental materials, equipment, transportation, licenses, etc...

- Charges for electrician, Generator Technician-Mechanic shall be used for the repairs of any generator(s) only.   No supplemental/special hourly rates will be paid for work performed beyond normal working hours, weekends, holidays or emergency declared situations. Overtime shall be paid only if trade personnel are required to work After-hours.

- For any necessary repair related work which is not considered part of the normal yearly major and minor maintenance services (inspections/testing’s), an approval shall be obtained from LDWF Facilities Maintenance Section and a written Notice to Proceed with the work shall be necessary. Notice to Proceed should describe the work to be performed and an estimated cost for the work.

Quantities listed for labor related items of work have been estimated and are for bidding purposes only. Actual quantities may be more or less than the estimated bid quantities. Quantities shown have been based on a period of one year