**If bidding other than specified, please provide manufacturer’s specs for “or equal” items. **

Scope of Work:

The Contractor shall provide all labor, materials, equipment, supervision, and services necessary to remove and replace the existing nine morgue bays with nine new, fully compliant, modern morgue cooler units for the Eastern LA Mental Health System (ELMHS).

Location:

Eastern Mental Health System

4502 Hwy 951

Jackson, LA 70748

Agency Contact

Jonathan Holley or Dylan Fury

225-634-0202

Specifications:

The Contractor shall be responsible for the following:

Demolition

- Safely disconnect and remove existing nine morgue bays

- Dispose of equipment in accordance with all regulations

- Protect surrounding facility areas during removal

Temporary Morgue Services

- Provide a fully operational temporary morgue unit on-site

- Maintain full-service capacity during construction

- Remove temporary unit after project completion

New Morgue System Installation

- Install all associated refrigeration, electrical, and control systems

Testing, Commissioning & Training

- Test and verify full system operation

- Provide staff training and all manuals/warranties

Morgue Refrigeration Units

Brand/Model: AWIC – Series HPPS or Equal

Specify Brand/Model Bidding: ____________________

- Temperature Range: 34°F to 39°F (1°C to 4°C) for standard storage

- Freezer Option (if applicable): -10°F to 0°F

- Temperature Control: Digital thermostat with external display

- Alarm System: Audible and visual alarms for temperature deviation

- Refrigerant: Environmentally compliant (EPA-approved)

- Cooling Type: Self-contained or remote system (as required by site conditions)

Construction & Materials

- Nine individual body storage bays

- Tray System: Heavy-duty stainless steel roller trays

- Load Capacity: Minimum 300–350 lbs per tray

- Doors: Insulated, gasket-sealed with heavy-duty hinges and latches

- Identification: External labeling system for each bay

Electrical Requirements

- Voltage: 208/230V or 460V (verify site conditions)

- Phase: Single or three-phase as required

- Dedicated circuits for refrigeration units

- Emergency power compatibility (tie-in to generator if available)

Energy Efficiency

- Units shall be energy-efficient and designed to reduce operational costs

- High-efficiency compressors and insulation required

- LED interior lighting (if applicable)

Controls & Monitoring

- Digital control panel with temperature readout

- Remote monitoring capability

- High/low temperature alarms with notification capability

Compliance Requirement

- Must meet all applicable:

  - State and local health codes

  - OSHA safety standards

  - CDC infection control guidelines

  - Applicable electrical and mechanical codes

General Terms/Conditions:

- The Contractor shall coordinate work to minimize disruption.

- The Contractor shall maintain a safe and clean work environment.

- The Contractor shall obtain all permits and inspections.

- The Contractor shall provide project timeline prior to start.

- Temporary morgue shall be operational before demolition.

- Ensure continuous service with no downtime.

- Minimum 1 year labor warranty

- Manufacturer warranty on all equipment

- The Contractor shall provide service contacts and response times.