**If bidding other than specified, please provide manufacturer’s specs for “or equal” items. **

Scope of Work:

The Contractor shall provide all labor, materials, equipment, supervision, and services necessary to remove of two damaged condenser coils and install two new chiller condenser coils on Chiller #2 Circuit #1 and Circuit #2 for the New Orleans Center for Creative Arts (NOCCA).

Location:

New Orleans Center for Creative Arts (NOCCA)

2800 Chartres St.

New Orleans, LA 70117

Agency Contact

Joe Johnson

jjohnson@nocca.com

(504) 940-2813

Specifications:

The Contractor shall be responsible for the following:

Chiller Model: YVAA0323EKF46BAV

Serial #: 11531F42758070

- Recover and weigh refrigerant from Chiller #2- Circuit #1 and Circuit #2

- Remove and dispose of two existing condenser coils that are damaged on Chiller #2 Circuit #1 and Circuit #2 and remove angle valves on Circuit #1 and Circuit #2.

- Furnish and install two condenser coils on Chiller #2 Circuit # 1 and Circuit #2 and furnish and install angle valves for Circuit #1 and Circuit #2. York OEM parts or Equal

Specify Brand/Model Bidding: __________________

- Furnish & install four new drier cores on each circuit.

- Pressurize the system, perform leak check and pull vacuum on Circuit #1 and Circuit #2

- Confirm micron level and recharge circuit with new and recovered refrigerant.

- Perform test of system and monitor for proper operation.

- Clean up the work area to pre-work conditions upon completion of the project.

Any defective parts or other defects found during the installation of the condenser coils shall not be replaced or repaired without prior approval of NOCCA.

General Terms/Conditions:

- All work being performed is required during normal business hours. Monday through Friday 7:30 A.M. - 4:00 P.M. excluding agency holidays.

- Work to be performed in a workmanlike manner according to standard, and meet all code requirements, federal, state, and local.

- All equipment should have a minimum of one year manufacturer’s warranty. Workmanship shall be covered by a one year warranty for installation work.

- Vendor representatives must follow all agency policy and procedures while performing work on facility grounds.

- The Contractor is subject to a conference/training with facility staff after the contract is executed and before performing any work.

- All waste and debris are removed from the site daily and disposed of properly with the exception of any equipment that is accounted for through property control measures by the Contractor. All waste/debris must be assessed by the appropriate site staff before it is removed from the site.