Attachment B

RFx number: 3000026186

Contract Title: Portable Fire Extinguishers - Statewide

Specifications

# Scope:

This specification covers Portable Fire Extinguishers for use by State of Louisiana agencies.

# Classification:

Class, weight and rating: the fire extinguishers covered by this specification shall be the charges, classes, charge minimum weights and ratings as shown in the bid document.

The following documents form a part of this specification to the extent specified herein.

Underwriter’s Laboratories, Inc.:

Class A and Class B: C Fire Extinguishers

UL 154 - Carbon Dioxide Hand Fire Extinguishers

UL 299 - Dry Chemical Fire Extinguishers

UL 626 - Water-Type Fire Extinguishers

UL 711 - Rating and Fire Testing of Extinguishers

UL 1058 - Halogenated Agent Fire Extinguishers

National Fire Protection Association:

NFPA No. 10 - Portable Fire Extinguishers

# Requirements:

Label of Underwriter’s Laboratories, Inc.:

Bidder shall submit proof that the fire extinguisher they propose to supply under this specification conforms to applicable UL or Factory Mutual requirements. The UL or FM label permanently affixed to the extinguisher will be acceptable as evidence that the fire extinguisher conforms to this requirement.

Standard Product:

Each fire extinguisher furnished under this specification shall be a currently standard product of an established manufacturer. All accessories and components normally furnished commercially with the standard product offered under this specification shall be in the same quantity and of the same quality as furnished commercially with the standard product.

Design and Construction:

The fire extinguisher shall be designed and constructed to permit easy operation, inspection and maintenance. When UL or FM allows for an optional design feature, material or construction, the choice may be made by the manufacturer/contractor, provided it conforms to all other requirements of this specification.

Parts:

Aluminum parts shall be treated with chromate chemical conversion processor anodized to further inhibit effects of corrosion.

Exposed working parts (such as valves, springs and pins) in the discharge or actuating assemblies shall be made of suitable nonferrous metal or austenitic stainless steel. Operating levers and carrying handles, when they are a working part or locking means of the fire extinguisher, shall conform to this requirement.

Exterior Surfaces:

All exterior surfaces of fire extinguisher shells shall be treated or coated to resist normal atmospheric corrosion and shall be capable of passing the 240-hour salt spray test as described in UL specifications.

Charge:

The fire extinguishers shall be of the stored pressure variety, furnished with a standard charge conforming to the weight, classification and rating specified by the Using Agency, except that “water” type fire extinguishers shall be furnished dry (without charge).

Mounting Bracket:

A suitable mounting bracket, in conformity with UL requirements, shall be furnished with each fire extinguisher.

Coast Guard Approval:

All fire extinguishers, unless otherwise specified, shall be Coast Guard approved and shall conform to the applicable requirements of UL specifications in this regard.

Marking:

Operating, recharging and maintenance instructions shall appear on the container in conformance with UL requirements. Further, an instruction manual shall be provided giving condensed instructions and cautions necessary for the installation, operation, inspection and maintenance for each extinguisher.

Workmanship:

The fire extinguisher shall be constructed, assembled and finished to ensure good quality equipment.

Warranty:

Each extinguisher shall carry, at minimum, a 5-year manufacturer and vendor warranty.

Certification:

The bidder shall certify, by signing the bid, that the product offered meets this specification and that the product conforms to the manufacturer’s own drawings, specifications, standards and quality assurance practices and is the same product offered for sale in the commercial marketplace. The State of Louisiana reserves the right to require proof of such conformance at any time during the life of the contract.

# Preparation for Delivery:

Unit Packaging:

Each fire extinguisher shall be packaged in a close-fitting fiber board container with sufficient blocking and bracing to ensure safe handling and delivery to the receiving agency. The supplier’s standard commercial practice will be acceptable when it fulfills the preceding requirement.