# Scope of Maintenance Agreement

  - Preventative maintenance and repair services shall be provided by the Contractor on all equipment and associated devices related to the HVAC systems as outlined within these specifications. Work to be performed at the Old Governor’s Mansion located at 502 North Blvd, Baton Rouge, LA 70802

  - The Contractor shall furnish all personnel, parts, material, test equipment, tools and services in conformance with the terms and conditions as outlined below. If any part is deemed obsolete it must be replaced with a like in kind replacement. If a replacement is found not to be available it must be brought to the Old Governor’s Mansion Management.

  - It is the intention of this specification to establish and define those services that are to be performed.

  - The Contractor shall not be relieved from assuming all responsibility for properly estimating the difficulties and cost of performing the services required with this specification because of the failure to investigate the conditions or become acquainted with all the information concerning the services to be performed.

  - The Contractor shall utilize computer generated preventative maintenance directions which indicate task functions to be performed on each scheduled service call, as determined by calendar periods, operating hours (runtime), manufacturer’s recommendations, and historical data bank, as pertinent to each task.

  - As work is due, the Contractor shall issue to his technician on the job, the necessary and appropriate recommended maintenance procedures and a listing of any special lubricants and tools that are required for proper maintenance of the equipment.

  - The Contractor’s computer generated maintenance program shall provide for continuous updating of maintenance procedures and frequencies.  Breakdown experience and frequency shall determine the on-site material inventory level and preventative maintenance frequencies.

  - Conditioned space design conditions:	72 – 76 degrees F, 45 – 55% RH

  - The owner assumes that the system(s) being quoted upon is in a maintainable condition.  The successful bidder shall inspect all of the equipment 30 days prior to the start  of the contract to ensure that it is in working and operable condition.  The successful bidder shall have up to thirty (30) days to report, in writing to the Old Governor’s Mansion facilities manager or designated representative, all deficiencies and cost of necessary repairs.  If any deficiencies to the equipment are noted and repairs are needed, the owner reserves the right to determine who will make the necessary repairs.

# Equipment – Maintenance Service

  - Equipment Not Included

    - Maintenance service, including repair labor and parts replacement for portions of the systems and equipment that are non-maintainable or nonmoving are not required and not included as part of this specification.

    - Excluded items shall be considered as: foundations, structural supports, domestic water lines, drains, plumbing, oil lines, gas lines, piping, oil storage tanks, boiler shell and tubes, unit cabinets, boiler trim, refractory material, and cooling tower structure.

    - This specification covers only that equipment as listed herein, and in the event the system is altered, changed or equipment is added or not included in the specification, that portion shall be added or deleted as required and shall be in accordance with this specification.

  - Equipment Included

    - The specific quantities, sizes, and model numbers of the major pieces of equipment shall be listed separately on the EQUIPMENT LIST attached.

    - The preventative maintenance and the responsibility of the Contractor shall not be limited to only these major pieces of equipment as shown on the EQUIPMENT LIST, but shall also include all appurtenant devices and systems as listed below that are related to the heating, ventilating and air conditioning system.

      - Heating system – boilers, elements, furnaces, pumps, heating coils, steam traps, water strainers, unit heaters, duct heaters, heat exchangers, humidifiers, etc.

      - Cooling system – Chiller, cooling tower, air conditioning compressor(s), evaporative condensers, air cooled condensers, pumps, cooling coils, etc.

      - Air handling system – fans, motors, air filters, dampers, induction units, mixing boxes, fan coil units, etc.

      - Miscellaneous equipment – exhaust fans, manual valves, float valves, direct expansion valves, thermometers, gauges, magnetic starters, manual motor starter, pump and fan motor drives, belts, electrical wiring from motor starter to their respective motor(s), check valves, refrigerant piping and piping insulation.

      - Duct work – service work is to include all parts, materials and labor to maintain the entire existing ductwork throughout the building.

  - Services Included

    - The general services listed below shall apply to the systems and equipment as shown in the EQUIPMENT LIST.

      - Lubricate all equipment monthly and/or as needed to permit bearings, gears and all contract wearing points to operate freely and without undue wear.

      - Adjust all linkage, motors, drives, etc. that have drifted from the initial design setting and positions.

      - Calibrate all sensing, monitoring, output, safety, and optimum efficiencies.

      - Test and cycle all equipment as a system after is has been cleaned, lubricated, adjusted, and calibrated to assure that it is in proper operating condition and performing at optimum efficiency.

      - Replace 2” pleated filters monthly and/or upon request by OGM Facilities Manager.

      - Clean all components of dust, old lubricants, etc. to allow the equipment to function as designed.

      - Paint all equipment as needed to prevent and protect against corrosion and deterioration.

      - Examine each piece of equipment and device to see that it is functioning properly and in good operational condition.

      - Perform annual (or upon request) vibration analysis on all air-handling units and supply documented results within  15 days. This annual analysis shall be completed no later than December 30th of each year.

      - Perform annual (or upon request) vibration analysis on chillers and supply documented results within  15 days. This annual analysis shall be completed no later than December 30th of each year.

# Maintenance Procedures and Records

  - The contractor shall utilize computer generated preventative maintenance directions, which indicate task functions to be performed on each scheduled service call, as determined by calendar periods, operating hours (runtime), manufacturer’s recommendations, historical data bank, as pertinent to each task.  Detailed written service reports shall be submitted to the OGM Facilities Manager at the time of service.

  - The Contractor shall communicate with the OGM Facilities Manager or representative on a daily or as needed basis by utilizing e-mail as communication in addition to telephone and fax.  Contractor shall respond accordingly same means of communication within 24 hours.

  - During the course of this service, the Contractor shall advise and assist in the determination of improvements to the mechanical system that shall conserve energy and minimize utility expenditures.

  - The Contractor routine preventative monthly maintenance shall be provided and completed no later than the first 10 normal work days of operation of each month.  Routine monthly preventative maintenance shall be scheduled at least 1 month in advance with the OGM Facilities Manager.

  - Parts to HVAC equipment vital to the operations that are in need of immediate repair shall be ordered the same day and shipped via Next Day Air.  All repairs to the operations deemed vital by the OGM Facilities Manager or representative shall be completed without delay.

    - HVAC equipment vital to the operation of the Old Governor’s Mansion include but not limited to:

      - Air-handlers (18)

      - Chiller (Carrier)

      - Cooling Tower

      - Boiler

      - Chill water pumps (2)

      - Hot water pumps (2)

      - Cooling Tower Pump (2) To include water treatment

      - Exhaust fans (7)

      - Hot water heater and circulation pump

      - Electrical

  - Contractor shall not remove or use any parts form other machinery for repairs.  All parts shall be replaced with newly manufactured parts of equal or greater value.  All repairs and replacement parts shall be noted, documented, and signed by the contracted service representative and OGM Facilities Manager or representative at the time of the service.  A copy of the report shall be given to the OGM Facilities Manager or representative at the time of service.

  - Subcontracting portions of systems or services requested in this specification shall only be allowed with prior consent from the OGM Facilities Manager or representative.  The OGM Facilities Manager shall reserve the right to interview and approve all subcontractors before the work is started.  Subcontractors approved shall continue their portion of maintenance work as long as the work remains acceptable to the Facilities Manager.

# Preventative Maintenance and Emergency Service Calls

  - The Contractor shall provide monthly preventive maintenance service and schedule at least 2 days in advance with the Facilities Manager.  Service shall be performed within the first 10 operating days of each month.

    - After each service call, a detailed service report shall be completed and left with the Facilities Manager or representative.

    - Two  of the scheduled service calls shall include the system startup and the system shutdown, for the appropriate season.

  - The Contractor shall provide emergency service on an as-required basis.  Emergency service shall be considered as called in addition to the scheduled preventative maintenance calls, but included in this agreement.

    - This emergency service shall be provided as often as needed, on a 24-hour basis, nights, weekends and legal holidays included.

    - The Service Company shall be capable of responding to an emergency situation within 2 hours.

    - The emergency service response system shall be a professionally manned telephone answering service.  Automatic telephone answering/recording machines or home telephone numbers are not acceptable.

  - The Contractor shall schedule quarterly, semi-annual and annual preventative maintenance services with the Facilities Manager no less than 2 days in advance.

    - Annual services shall be completed no later than December 30th of each year.  Failure to comply with specifications herein shall constitute cause for termination of the services and/or withholding of payment.

# Service Performance Guarantees

  - Performance Review

    - The owner’s agent may review, at any time, the services provided and reports submitted to verify that the preventative maintenance is in fact being properly and adequately performed.  Any lack of maintenance service shall be submitted to the Office of State Procurement in writing for corrective action.

    - Problems or deficiencies of significant importance or of a continual nature shall constitute cause for termination of the services and/or withholding of payment.

  - Guarantees

    - The Contractor shall maintain all instrumentation devices and systems in complete operating condition subject to the approval of the owner.  The Contractor, in effect, will guarantee these systems for the term of this contract.

    - The Contractor shall provide full maintenance and service of the entire system including replacement of the parts and materials for the entire term of the contract for any failures with the exception of those proven to be beyond the contractor’s control and as a direct result of but no limited to acts of government, strikes, lockouts, fire, explosion, riot, civil commotion, war, malicious mischief, flood, and other acts of God.  The cost of this maintenance and service shall be included in the cost of this contract.

  - Non-Performance

    - Failure to repair vital HVAC equipment within 2 days

    - Failure to answer calls and respond within 2 hours

    - Falsifying records

    - Failure to correct recurring problems of not more than three  attempts

    - Failure to submit service records at the time of service

    - Failure to submit test analysis reports within 30 days

    - Failure to perform annual vibration analysis on equipment specified

    - Failure to complete routine preventative monthly maintenance within the first 10 normal work days of operation of each month

    - Failure to replace filters as scheduled

    - Failure to schedule, and complete scheduled, quarterly, semi-annual and annual preventative maintenance

    - Failure to communicate with the Facility Manager or representative on a daily and/or on an as needed basis by email, telephone, or fax

    - Non-compliance with minimum performance standards

  - The owner reserves the right to have a consultant examine and provide a written report on conditions as found.  If such conditions are not corrected within 10 days by the HVAC Contractor, or the Contractor cannot furnish a valid documented reason for the delay, the owner reserves the right to employ another HVAC Contractor to complete the work.  The accumulated cost of such expenditures will be billed to the current HVAC Contractor.

  - The owner reserves the right to suspend payments at regular monthly billing rates and/or terminate the contract for non-compliance.

# Special Conditions

  - The successful bidder’s responsibility for injury to persons or property that may be caused by, or arise through the maintenance, service, functioning, or use of the system, shall be limited to injury caused directly by the Contractor’s obligations as set forth in this specification.

  - The successful bidder shall not be made liable for any loss, delay, injury, or damage, whether direct or consequential, that may be caused by proven conditions beyond the Contractor’s direct control including but not limited to proven acts of government, strikes, lockouts, fire, explosion, riot, civil commotion, war, malicious mischief, flood, and other acts of God.

# Preventative Maintenance Task Sheet

  - Cooling and Heating Equipment

    - Monthly Maintenance

      - Inspect overall unit for vibration and appearance; make adjustments/repairs as necessary

      - Inspect air filters and replace if necessary

      - Inspect condensate drain and clean if necessary

      - Inspect belts and adjust if necessary

      - Inspect bearings and grease if necessary

    - Quarterly Maintenance

      - Inspect bearings

      - Inspect belts

      - Inspect sheaves

      - Inspect squirrel cage

      - Inspect motor and electrical systems

      - Perform megohm test on motors (20 h/p and above)

      - Inspect coil for build-up of lint or dust

      - Inspect overall unit for vibration and appearance; make adjustments/repairs as necessary

      - Replace 2” pleated filters

    - Annual Maintenance

      - Perform vibration analysis

      - Inspect sheaves

      - Inspect bearings

      - Inspect belts

      - Inspect squirrel cage

      - Inspect motor and electrical systems

      - Perform megohm test on motors (20 h/p and above)

      - Inspect coil for build-up of lint or dust and clean coil if required or as requested

      - Inspect and clean fresh air intake grills (4)

      - Inspect overall unit for vibration and appearance; make adjustments/repairs as necessary

    - Annual Maintenance

      - Functionally check operation; make adjustments/repairs as necessary

      - Change oil, oil filters and air filter

      - Check belts; replace as necessary

      - Check batteries; replace as necessary

      - Change diesel oil filter(s)

      - Change air filter(s)

      - Test coolant; replace coolant every 2 years

      - Pressure test cooling system for leaks

      - Inspect fan belts; replace and adjust as required

      - Test oil heaters

      - Load test batteries

      - Inspect charging system and check operation

      - Megg generator starter coils

      - Check gauges for accuracy

      - Observe generator during exercise cycle

      - Run oil analysis on engine oil

  - Exhaust Fans

    - Quarterly Maintenance

      - Inspect sheave

      - Inspect bearings and grease as required or upon request

      - Inspect belts, tighten and/or replace as necessary or upon request

      - Inspect motors and electrical; make adjustments/repairs as necessary or upon request

  - Water Pumps

    - Monthly Maintenance

      - Inspect pump seal for excessive water loss; make adjustments/repairs as necessary or upon request

    - Quarterly Maintenance

      - Inspect pump seal for excessive water loss; make adjustments/repairs as necessary or upon request

      - Perform megohm test on motors (20 h/p and above)

      - Inspect and grease bearings

      - Inspect for vibrations, unusual noise, odors, etc.

      - Inspect packing; adjust to a slow drip if necessary

      - Inspect mechanical seal

      - Verify slow in sealing/flushing line

      - Lubricate coupling

      - Lubricate motor bearings

      - Inspect system for leaks in piping, flange connections, etc. and record condition

      - Clean ventilation openings (grills and/or screens)

      - Visually inspect coupling

      - Inspect contacts for signs of wear, arcing, overheating, etc., and record condition

      - Measure operating amperage and record readings

  - Hot Water Heaters

    - Monthly Maintenance

      - Check operation; make adjustments/repairs as necessary

      - Calibrate controls

      - Inspect general appearance

      - Check control set point and operation

      - Manually lift and reset relief valve

      - Record hot water supply

      - Bottom-blow heater tank to remove sediment

      - Check all wiring, insulation, and connections on heaters and controls

      - Check safety power out/off on heater

    - Annual Maintenance

      - Manually flush and try lever test pressure relief valve

      - Open and close isolation valves and check piping and valves for leaks

      - Check heater current and voltage

      - Check condition of anode rod

      - Check control setting and operation

      - Bottom-blow heater tank to remove sediment

      - Record hot water supply temperature

# Contractor Qualifications

  - The following requirements shall be considered as the minimum standards for the employees of the Contractor to be considered as qualified to provide services under this contract, and shall be a prerequisite to any award.

    - The Contractor shall have a permanent office In the State of Louisiana.  The Contractor shall supply the Old Governor’s Mansion with a single telephone number, which shall be answered by a Contractor representative between the hours of 8:00 AM and 4:30 PM CT, Monday through Friday.  The same number shall be answered after normal hours and on weekends and holidays.  Telephone answering systems are not acceptable.

    - The Contractor shall, no later than 5 working days before a technician is scheduled to begin performing maintenance tasks, submit to the Old Governor’s Mansion a resume for each HVAC technician he proposes to employ either initially or as a replacement.  Resumes must be submitted prior to the assignment of any technician.

    - The Contractor shall employ certified, qualified and trained service personnel to perform the services that are to be provided.  The Facilities Manager shall reserve the right to require that the Contractor dismiss any and all unacceptable personnel for due and just cause as determined by the Facilities Manager.

    - The Contractor’s preventative maintenance program shall be computer generated, based on run time, manufacturer’s recommendations, and historical data bank on similar equipment.  Simple computer based, run time only, or hand scheduled programs are not acceptable.

    - The Contractor shall actively employ a minimum of five  HVAC journeyman class service technicians.  Journeyman shall have a minimum of 3 years of experience at the journeyman level.

    - Each resume shall contain at least the information described below.  Additional information which demonstrates the proposed employee’s knowledge, skill and experience is encourages.

    - Subcontracting portions of the services requested in this specification shall not be allowed without prior consent from the Facilities Manager.  The OGM personnel shall have the right to interview and to approve the subcontractors.  Subcontractors approved shall continue their portion of the maintenance work as long as the work remains acceptable to the Old Governor’s Mansion.

    - Copies of certification cards shall be submitted, upon request, before the contract is awarded.  HVAC service technicians must be full time employees of the Contractor.

    - Helpers shall have a minimum of 2 years of general experience in HVAC maintenance work.  Helpers may be used to assist HVAC technicians.  Helpers may not perform journeyman level tasks unless he is performing those tasks under the direct supervision of a journeyman.  Helpers may not perform any maintenance tasks unless a journeyman is in the building.

| Equipment | Description | Valid To | Planning plant | Functional Loc. | Description |
| --- | --- | --- | --- | --- | --- |
| 10029586 | Air Handling Unit 1 K98D26528 | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10029592 | Air Handling Unit 10 K98D26564 | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10029601 | Air Handling Unit 11 K98D26393 | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10029611 | Air Handling Unit 12 K98D26428 | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10029621 | Air Handling Unit 13 K98E39270 | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10029625 | Air Handling Unit 14 K98D26453 | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10029628 | Air Handling Unit 15 K98D26498 | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10029686 | Air Handling Unit 3 K98D26586 | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10029713 | Air Handling Unit 4 K98D26544 | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10029741 | Air Handling Unit 5 K98D27610 | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10029768 | Air Handling Unit 6 K98D26474 | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10029790 | Air Handling Unit 7 K98D26509 | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10029810 | Air Handling Unit 8 K98D26525 | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10029824 | Air Handling Unit 9 K98D26553 | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10029939 | Boiler 1 AJAX WNG700 | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10029988 | Chill Water Pump 1 AURORA | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10030052 | Chiller 1 Carrier | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10030108 | Condenser Pump 1 (Equip. Room 6) AURORA | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10030149 | Cooling Tower 1 Evapco | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10030280 | Exhaust Fan 1 (Equip. Room - 1) | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10030291 | Exhaust Fan 2 (Roof) | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10030398 | Hot Water Heater (50 gallon) RHEEM | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10030441 | Hot Water Heater Pump 1 AURORA | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |
| 10030561 | Refrigerant Leak Detector TRANE | 12/31/9999 107A |  | LA-2-17-026-BLD-000001-01-107A | OLD GOVERNOR'S MANSION - 107A |