**If bidding other than specified, please provide manufacturer’s specs for “or equal” items. **

Scope of Work

The Contractor shall supply all labor, rentals, permits and materials to remove and install a double wall fire-protected aboveground storage tank for the Department of Corrections (DOC).

Location:

Louisiana Correctional Institute for Women

6923 Highway 74

St. Gabriel, LA 70776

Site Visit Contact:

Clarence Bourgeois; (225) 354-6949

Jeff Ridgel; (985) 269-4160

Specifications:

The Contractor shall be responsible for the following:

- Supply and install one 6,000-gallon 96” Fireguard Dual Compartment (4k/2k) or Equal

Specify Brand/Model Bidding: _______________________

- The tank shall have steel outer walls to provide low cost maintenance and protection.

  - Primary storage tank and secondary containment shall be compatible with a wide range of fuels and chemicals, including biodiesel & ethanol

  - There shall be thermal insulation material that exceeds the UL 2-hour fire test.

  - The approximate diameter is 102" and length is 198".

- The Contractor shall provide a crane to offload the tank from the delivery truck and install a 20' x 24' slab with bollards for tank installation.

- The Contractor shall include all required electrical piping required for the project.

The Contractor shall supply and install the following:

- One 2-product remote fill box with all necessary piping

- Two FE Petro or Equal 1-1/2 hp submerged motors with leak detectors

Specify Brand/Model Bidding: _______________________

- 2" black iron product piping with all necessary solenoid valve, ball valves, pressure relief valves and any other required valves.

- Two dispenser pedestals under dispenser containment sumps with all necessary shear valves Morrison Bros. CO 434 Series dispenser pedestal or Equal

Specify Brand/Model Bidding: _______________________

  - The pedestal shall be 12-gauge steel, black powder coated

  - Pre-drilled anchor holes

  - The dispenser mounting platform shall overhang the pedestal base minimizing the ability for water penetration.

  - The stabilizer bar kit shall be included by the Contractor.

  - Connection boots available

Single Remote Dispenser:

Brand: Wayne Select or Equal

Specify Brand/Model Bidding: _______________________

- Flow Control Valve: proportional 7/8'' (2.2 cm). allows setting max. flow rate. SHC uses two valves.

- Inlet Connection: 1 1/2'' (3.8 cm) male. NPT. (e85 option - 1 1/2'' (3.8 cm) fem. NPT. no riser).

- Discharge: 1'' female NPT w/ 3/4'' adapter.

- DEF: w/ 1'' male BSPP adapter.

- Hose Hanger: Keeps hose off ground when idle.

- Electrical: 120 vac 60 Hz

- Pressure: Working pressure up to 50 psi.

- Cabinet finish: powder-coated metallic silver sides, top, and base

  - Doors powder-coated blue.

  - Charcoal gray bezel with matching decal with white lettering.

- Cabinet Construction: All exterior panels are fabricated from heavy gauge galvannealed steel for superior weather and corrosion resistance.

  - Hinged doors for convenient service access.

  - Totalizer: 7-digit electromechanical non-resettable totalizer per hose.

- Fuel control system interfaces: Wayne protocol. optional pulse output.

- Nozzle boot: fits UL interchangeable nozzles and Emco Wheaton 4015 and Husky V short spout balance vapor recovery nozzles.

- Actual Dimensions: 32.25'' w x 19.38'' d x 63.3'' h (81.9 cm w x 49.2 cm d x 160.8 cm h)

- One Ultimate Automatic Tank Gauging System Maglink LX or Equal:

Specify Brand/Model Bidding: _______________________

Shall Include:

  - Display

  - Printer

  - Two 101” inventory only tank probes with floats

  - Two sump sensors

  - One interstice sensor

  - One overfill alarm

General Terms:

- The Contractor shall be responsible for delivery and pickup of materials/supplies needed to complete project.

- Disposal of all materials and debris shall be the responsibility of the Contractor.

- The Contractor shall be responsible for providing any lifting capability to complete all new installations and repairs.

- The Contractor shall take all precautions necessary to prevent damages when making repairs. This includes movement and parking of equipment on grass or unimproved areas surrounding site.

- The Contractor shall contact, prior to mobilization and demobilization, the Project Manager for staging and for satisfactory completion.