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October 29, 2026

Addendum No. 01 

Your reference is directed to RFx Number 3000026811 for the Invitation to Bid (ITB) for the State of Louisiana – Transmission Line Installation - LETA, which is currently scheduled to open at 10:00 AM CT on 11/05/2026.

The following are the Vendor’s Inquiries received by the deadline date of October 22, 2026, and the State’s Responses:

Vendor’s Inquiry #1: Attachment D Tower Details and Photo’s Details list section indicates a number of missing hangers and other items denoted as needing service, replacement or repair; is the installation Contractor responsible within this scope to provide corrective action to the items denoted from Section 5 through Section #36?

State’s Response #1: No corrective action is required of the installation Contractor regarding pre-existing issues described or detailed in Attachment D.

Vendor’s Inquiry #2: With regards to Specification sections related to the removal of the existing 4 1/16 hangers and line to be delivered to 3413 Phillips Road Rayne, LA; A.) Is the Contractor responsible for offloading these materials? 
B.) Will secure storage be provided for the offloaded materials such as inside the transmitter building or into a secure weather protected Conex box?
C.) Please confirm the Contractor is not responsible for the condition of the 4 1/16” line and the requirement is for transport “as is” with respect to quantity and condition

State’s Response #2: 
A.) Yes. 
B.) Secure storage will be provided inside the transmitter building and must be coordinated with the facility point of contact.
C.) All 4 1/16” line removed must be removed and preserved in its original state for potential re-use at the KLPB site to which it is being delivered (3413 Phillips Rd., Rayne, LA). Delivery of the removed 4 1/16” and hangars to the KLPB site shall be “FOB Destination”. Therefore, the installation Contractor will bear risks of damage, loss, or delay while the 4 1/16” line and hangars are in transit to the KLPB site. 


Vendor’s Inquiry #3: Will the Contractor or WLPB be responsible for commissioning of the 7 3/16 line system into the WLPB transmission system beyond the line sweep such as;
a. Proof of Performance
b. TPO, VSWR, other calibrations assumed to be affected by the lower line loss of the new line replacing the existing 4 1/16” line.

State’s Response #3: With regard to commissioning of the 7 3/16” line system, the installation Contractor will only be responsible for the line sweep.

Vendor’s Inquiry #4: With reference to “Provide a rigging plan” denoted within the specifications; can WLPB please provide a current structural analysis reflecting suitability of the structure for the 7 3/16” transmission line replacing the 4 1/16’ to prepare the required rigging plan 

State’s Response #4: Structural analysis will be commissioned separately by the State Agency and provided to the installation Contractor.

Vendor’s Inquiry #5: Will the Contractor be allowed to provide adapter plates to allow installation of the new 7 3/16” hangers, replacing the existing 4 1/16” hangers or will the Contractor be required to drill new holes if necessary to accommodate the larger 7 3/16” hangers?

State’s Response #5: The installation Contractor shall coordinate a site visit with the facility point of contact in order to make this determination.

Vendor’s Inquiry #6: Please confirm if the Contractor or WLPB will be responsible for providing any dumpster for packaging, pallets, skids or others packing materials from the job site?

State’s Response #6: The installation Contractor will be responsible for providing any dumpster for packaging, pallets, skids or others packing materials.

Vendor’s Inquiry #7: Will the WLPB materials provided be stored inside or in a secure storage container provided by WLPB.

State’s Response #7: This determination will be made by the State Agency in coordination with the materials vendor.

Vendor’s Inquiry #8: Confirm all materials including custom cut coax sections, elbow complex’s upper and lower, will be provided by WLPB at time of work start or will additional days need to be included to allow order and shipment of any custom dimension 7 3/16” associated materials?


State’s Response #8: The following items will be procured by the State Agency through a materials vendor:
 
· 1,160 feet of 7 3/16" transmission line for 996 feet vertical and 170 feet horizontal run.

· Hanger(s) as required by the manufacturer for both horizontal and vertical runs.

· One O ring kit for the line.

· One Gas stop for 7 3/16" line.

· Two transition from 7 3/16 to 6 1/8-inch 75 ohm.

· One transition from 6 1/8-inch 75 ohm to 6 1/8-inch 50 ohm.

· One 6 1/8-inch 75-ohm fine matcher.

· Four 7 3/16-inch reinforced elbows.

· One dehydrator

· One feed through plant for 7 3/16" line for building penetration.

· One System sweep

· Four 7 3/16" flanges

Vendor’s Inquiry #9: Will the Contractor or WLPB be responsible for any rain or weather delays incurred during the installation in addition and separate from the Contractors price?

State’s Response #9: The installation Contractor will be responsible for all weather delays, the cost of which should be included within the scope of the Contractor’s bid pricing.

Vendor’s Inquiry #10: What is the desired date for work start, assuming the materials must be ordered and delivered by WLPB?

State’s Response #10: As soon as practicable and in coordination with State Agency and materials vendor.

Vendor’s Inquiry #11: Is there a deadline for completion and any blackout dates the Contractor will not be able or required to work around during the installation?


State’s Response #11: Deadline for completion is June 30, 2027. No blackout dates are anticipated.

Vendor’s Inquiry #12: Confirm WLPB will manage all FCC STA, CP, and license filings as result of the changes to WLPB’s current licensed parameters?

State’s Response #12: Confirmed, WLPB will manage all FCC STA, CP, and license filings as result of the changes to WLPB’s current licensed parameters

Vendor’s Inquiry #13: Should there be any delays not caused by the contractor to accommodate a single mobilization work start to work completion, will WLPB or contractor be responsible for additional costs of a work stoppage, delay, or remobilizations should they occur?

State’s Response #13: The installation Contractor will be responsible for the cost of any such delays, which should be included within the scope of the Contractor’s bid pricing.


All else remains as on original Invitation to Bid.


This addendum is hereby officially made a part of the referenced solicitation. 
Acknowledgement: If you have already submitted your bid and this Addendum does not cause you to revise your bid, you should acknowledge receipt of this Addendum by identifying your business name and by signing where indicated.  You may return this Acknowledgement by mail or delivery by hand or courier to: Office of State Procurement, 1201 N. 3rd Street, Ste. 2-160, Baton Rouge, LA  70802, or by fax to: (225) 342-9756.  The State reserves the right to request a completed Acknowledgement at any time.  Failure to execute an Acknowledgement shall not relieve the bidder from complying with the terms of its bid.
Addendum Acknowledged/No changes:

For:  ________________________  By:  __________________________



Revision: If you have already submitted your bid and this Addendum requires you to revise your bid, you must indicate any change(s) below, identify your business name and sign where shown.  Revisions shall be delivered prior to bid opening by mail or delivery by hand or courier to: Office of State Procurement, 1201 N. 3rd Street, Ste. 2-160, Baton Rouge, LA  70802, or by fax to: (225) 342-9756, and indicate the RFx number and the bid opening date and time on the outside of the envelope for proper identification.  Electronic transmissions other than by fax are not being accepted at this time.


Revisions received after bid opening shall not be considered and you shall be held to your original bid.

Revision:

For:  ________________________  By:  __________________________


By:	Arkeith White
	Office of State Procurement
	Telephone No. 225-219-4207
	Email:  Arkeith.white@la.gov
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