Attachment C – Specifications
RFx 3000026852

**If bidding other than specified, please provide manufacturer’s specs for “or equal” items. **
Scope of Work: 
The Contractor shall supply all labor, equipment, and materials to install four standby generator systems complete with four Automatic Transfer Switches for the Louisiana Department of Health (LDH).

Location: 
Villa Feliciana Medical Complex 
5002 Hwy 10
Jackson, La 70748

Agency Contact:
Derick Herring - (225) 634-4086 
Daniel Gore - (225) 634-4090

Specifications:
The Contractor shall be responsible for the following:
150kW Standby Diesel Generator – for Sewer Plant
· The Contractor shall provide and install Blue Star JD150-01 or Equal
Specify Brand/Model Bidding: ____________________
· Rating: 480/277V, 3 Phase, 60Hz, 0.8 PF
· KW: 150kW 
· Deep Sea Controller with Remote Annunciator Enclosure
· Emergency Stop Kit 
· Level 1 Weather Enclosure, powder-coated, 14-gauge steel, 200 MPH wind-rated
· Critical Grade Exhaust Silencer
· 96-hour (1,500-gallon) UL-142 Double Wall Sub-base Fuel Tank
· 225 Amp, 3-Pole, 600V Main Circuit Breaker
· Engine Block Heater: 2000W, 240V
· 12V 10A Battery Charger
· 2-Year / 2,000-Hour Limited Warranty
Automatic Transfer Switch (ATS) – for Sewer Plant
· The Contractor shall provide and install ASCO 300 Series or Equal

Specify Brand/Model Bidding: ____________________
· Rating: 225A, 480V, 3 Phase
· Controller: 300 Series with 11BE Exerciser Kit
· Service Entrance Rated, 3-Pole with Solid Neutral, Delayed Transition
· NEMA 3R Enclosure with 44G Strip Heater
· 2-Year Limited Warranty
60kW Standby Diesel Generator – for Recreation Building
· The Contractor shall provide and install Blue Star JD60-02 or Equal
Specify Brand/Model Bidding: ____________________

· Rating: 208/120V, 3 Phase, 60Hz, 0.8 PF
· KW: 60kW 
· Deep Sea Controller with Remote Annunciator Enclosure
· Emergency Stop Kit 
· Level 1 Weather Enclosure, powder-coated, 14-gauge steel, 200 MPH wind-rated
· Critical Grade Exhaust Silencer
· 96-hour (1,500-gallon) UL-142 Double Wall Sub-base Fuel Tank
· 225 Amp, 3-Pole, 240V Main Circuit Breaker
· Engine Block Heater: 1500W, 120V
· 12V 10A Battery Charger
· 2-Year / 2,000-Hour Limited Warranty
Automatic Transfer Switch (ATS) – for Recreation Building
· The Contractor shall provide and install ASCO 300 Series or Equal
Specify Brand/Model Bidding: ____________________
· Rating: 200A, 208V, 3 Phase
· Controller: 300 Series with 11BE Exerciser Kit
· Service Entrance Rated, 3-Pole with Solid Neutral, Delayed Transition
· NEMA 3R Enclosure with 44G Strip Heater
· 2-Year Limited Warranty
125kW Standby Diesel Generator – for Residences 2, 3, 4, & 5
· The Contractor shall provide and install Blue Star JD125 or Equal

Specify Brand/Model Bidding: ____________________


· Rating: 208/120V, 3 Phase, 60Hz, 0.8 PF
· KW: 125kW 
· Emergency Stop Kit 
· Level 1 Weather Enclosure, powder-coated, 14-gauge steel, 200 MPH wind-rated
· Critical Grade Exhaust Silencer
· 96-hour (1,500-gallon) UL-142 Double Wall Sub-base Fuel Tank
· 225 Amp, 3-Pole, 240V Main Circuit Breaker
· Engine Block Heater: 1500W, 120V
· 12V 10A Battery Charger
· 2-Year / 2,000-Hour Limited Warranty
Automatic Transfer Switch (ATS) – Residences 2, 3, 4, & 5
· The Contractor shall provide and install ASCO 300 Series or Equal

Specify Brand/Model Bidding: ____________________

· Rating: 400A, 208V, 3 Phase
· Controller: 300 Series with 11BE Exerciser Kit
· Service Entrance Rated, 3-Pole with Solid Neutral, Delayed Transition
· NEMA 3R Enclosure with 44G Strip Heater
· 2-Year Limited Warranty
30kW Standby Natural Gas Generator – for Residence #1
· The Contractor shall provide and install Kohler Standby Whole Home Generator or Equal
· 
Specify Brand/Model Bidding: ____________________

· Rating: 208/120V, 3 Phase, 60Hz, 0.8 PF
· KW: 30kW 
· Deep Sea Controller with Remote Annunciator Enclosure
· Emergency Stop Kit 
· Level 1 Weather Enclosure, powder-coated, 14-gauge steel, 200 MPH wind-rated
· Critical Grade Exhaust Silencer
· 225 Amp, 3-Pole, 240V Main Circuit Breaker
· Engine Block Heater: 1500W, 120V
· 12V 10A Battery Charger
· 2-Year / 2,000-Hour Limited Warranty

Automatic Transfer Switch (ATS) – for Residence #1
· The Contractor shall provide and install ASCO 300 Series or Equal

Specify Brand/Model Bidding: ____________________

· Rating: 200A, 208V, 3 Phase
· Controller: 300 Series with 11BE Exerciser Kit
· Service Entrance Rated, 3-Pole with Solid Neutral, Delayed Transition
· NEMA 3R Enclosure with 44G Strip Heater
· 2-Year Limited Warranty

Concrete Foundations
The Contractor shall provide:
· Four Generator Pads: Reinforced with rebar
· Four ATS Pads: Reinforced with rebar
· Concrete shall meet applicable structural standards for equipment loading and vibration control.

Generator Installation
· The Contractor shall set and secure generators on the prepared concrete pads.

· The Contractor shall install all required control cables, main power cables, and two dedicated circuits each for the battery chargers and block heaters.

Automatic Transfer Switch (ATS)
· The Contractor shall mount and secure ATS on concrete pads.

· The Contractor shall coordinate scheduled shutdown for final connections between ATS, building service, and transformer.

· The Contractor shall terminate and label all power and control wiring per code and manufacturer standards.

Remote Annunciator Panels and Remote Emergency Stops
· The Contractor shall install conduit from generator through concrete slab to each building.

· The Contractor shall mount and wire remote annunciator panel inside each building.

· The Contractor shall install remote emergency stop button in a breaker glass enclosure in an accessible and code-compliant location for each.



Fueling
· The Contractor shall supply and fill fuel to 80% of each tank’s capacity using Clear Diesel (on road).

Load Testing
· The Contractor shall perform 2-hour load bank test:
· 30 minutes at 50% load
· 1.5 hours at 80% load

· The Contractor shall conduct 1-hour building load transfer test (to be coordinated with LDH’s representative).

Functional Testing
· The Contractor shall verify all generator and ATS operations, alarms, safety interlocks, and control functions.

· The Contractor shall confirm proper function of remote annunciator and emergency stop circuits.

Training and Demonstration
· The Contractor shall conduct operational demonstration with the project coordinator and facility maintenance personnel.

· The Contractor shall provide training on start-up, shut-down, fault response, and maintenance requirements.

General Terms:
· All work shall comply with local building, electrical, and fire codes.

· The Contractor shall coordinate with facility management to minimize downtime.

· The Contractor shall provide all necessary equipment, labor, materials, and permits.

· All materials and workmanship shall be guaranteed for a minimum of one year from final acceptance unless otherwise stated by manufacturer warranty.

· On site work schedule is Monday – Friday, 7:00am to 3:30pm.
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